6. ENGINEERING SYSTEMS REQUIREMENTS

G30 SITE CIVIL/MECHANICAL UTILITIES

********************************************************************************************************** 
SYSTEMS REQUIREMENTS
SITE CIVIL/MECHANICAL UTILITIES TEMPLATE 09/22

Instructions for using this template: There are template files for each UNIFORMAT Level 2 Group Elements. This template is for Group Element G30-SITE CIVIL/MECHANICAL UTILITIES. Text such as this is hidden text that will not print when the hidden text box in "Print/Options" is un-checked.

The Civil and Mechanical Member must edit this template for the requirements of the project. The SYSTEMS REQUIREMENTS are intended to define items that are required for these utility systems. Editing is required where brackets [ ] appear. Delete all utility elements that are not required for the project. If additional elements or sub-elements are required for the project that do not appear in the template, refer to the NIST UNIFORMAT II publication for additional site element numbers and descriptions. The Uniformat II Work Breakdown Structure can be found at www.wbdg.org/ndbm/ . Coordinate with the PERFORMANCE TECHNICAL SPECIFICATION SECTION G30 to ensure that performance requirements are provided for all of the Utility Elements listed here and that paragraph numbering matches.
**********************************************************************************************************

********************************************************************************************************** 
NOTE:  Edit the following paragraphs to suit the project, or create your own, to describe the SITE CIVIL/MECHANICAL UTILITIES for the project.  Coordinate this section carefully with other portions of the RFP.
**********************************************************************************************************

********************************************************************************************************** 
NOTE:  Consider site improvement activities and components relative to Part 2 UFGS Section 01 33 29, Sustainability Requirements and Reporting, and UFC 1-200-02, High Performance and Sustainable Building Requirements.
**********************************************************************************************************

SYSTEM DESCRIPTION
********************************************************************************************************** 
NOTE:  This specification assumes a project will utilize installation-owned utility systems.  Should any utilities be owned by a non-installation entity, RFP Editor will need to coordinate with the utility owner for system requirements and make necessary modifications to this ESR and corresponding PTS G30.
**********************************************************************************************************

The site civil/mechanical utility systems include water supply systems, sanitary sewer systems, storm drainage systems, heating distribution systems, cooling distribution systems, fuel distribution systems and associated appurtenances which are more than 5 feet (1.5 meters) outside the building.

The site mechanical utility system consists of piping and appurtenances for [steam] [and] [condensate,] [steam manholes,] [chilled water,] [hot water] [liquid fuel,] [natural gas,] and [propane] [    ] including accessories and devices as required for a complete and usable system up to 5 feet (1.5 meters) outside buildings.

GENERAL SYSTEM REQUIREMENTS
********************************************************************************************************** 
NOTE:  A blank Permits Record of Decision (PROD) form is included in Part 6 of the Standard Template Complete Set zip file on the WBDG Design-Build Request for Proposal page.
 **********************************************************************************************************

Develop the site to provide water, fire protection, sanitary sewer, storm drainage, heating, cooling and fuel distribution services that meet the requirements of each regulatory agency that governs and issues permits for the construction and operation of these systems. Site design is required to comply with UFC 3-210-10, Low Impact Development, as well as state or local stormwater management regulations and project sustainability goals.

Provide each system complete and ready for operation.

Physically verify the location of existing above and below ground utilities prior to starting work.

Identify and obtain permits to comply with all federal, state, and local regulatory requirements associated with this work.  Complete the Permits Record of Decision (PROD) form with the first design submittal package.  Determine correct permit fees and pay said fees.  Forward copies of permits, permit applications, and the completed PROD form to the Government's Civil/Mechanical Reviewer. Perform work in accordance with the obtained permits.

Minimize the impact of construction activity on facility operations and neighboring facilities.

Utility connection points are indicated on the drawings in Part 6. Obtain final approvals from the Government's Civil/Mechanical Reviewer and the Contracting Officer for utility connection points associated with this work.

Coordinate with the local utility providers and pay fees or charges required to connect to their utility.

Disciplines involved in site work design must coordinate utility locations with the Civil Engineer and the Landscape Architect.

Refer to Site Analysis and Building Requirements Sections for additional site civil/mechanical utilities information.

Provide fittings, connections and accessories required for a complete and usable system. Install equipment in accordance with PTS Section G30 and the manufacturer's recommendations. Where the word "should" is used in the manufacturer's recommendations, substitute the word "must".

See UFGS 01 78 23 OPERATION AND MAINTENANCE DATA for additional requirements.

Provide site civil/mechanical utility systems and components that support project sustainability goals of Part 2 UFGS Section 01 33 29, Sustainability Requirements and Reporting.

********************************************************************************************************** 
NOTE:  Use BMS B-5.2.19 to determine installation requirements for connecting to existing sanitary sewer lines and incorporate into this paragraph.
 **********************************************************************************************************

Verify the sanitary sewer connection to the sanitary sewer system by visual testing.  [Perform post-installation TV inspection of new sanitary sewer mains.]  Complete a visual inspection[, dye test][ and smoke test].

Leakage test is [not] required.

[Perform post-installation TV inspection of new storm sewer mains.]

G3030 STORM SEWER

**********************************************************************************************************

NOTE: For most projects the new storm sewer system is an extension of an existing storm sewer system.  Where a new storm sewer system is proposed, revise wording in the paragraph below.

Background information on Low Impact Development policy was introduced in Part 3 Project Objectives.  Storm sewer combines Navy LID policy and reporting requirements in FC 1-300-09N Navy and Marine Corps Design Procedures, storm sewer criteria in UFC 3-201-01 Civil Engineeringand LID criteria in UFC 3-210-10 Low Impact Development.

**********************************************************************************************************

The new storm sewer system is an extension of the existing storm sewer system.  The existing storm sewer system serving the project site is [owned by the Federal Government] [operated and maintained by [_____ (utility provider)] at [_____ (utility address)] and [_____ (utility phone number)]].  Provide the new storm sewer system and connections to the existing storm sewer system in accordance with [the utility provider's requirements,] UFC 3-201-01 Civil Engineering; UFC 3-210-10 Low Impact Development and FC 1-300-09N Navy and Marine Corps Design Procedures, state stormwater management laws and regulations, local stormwater management laws and regulations and project sustainability goals; whichever is more stringent.

********************************************************************************************************** 
NOTE:  If outfall for existing storm sewer system is located off the Activity, require Contractor to determine that existing outfall has adequate capacity to handle additional flow generated by project.  Also require Contractor to obtain approval from system owner and provide a copy of all correspondence to the Government Civil Reviewer.
**********************************************************************************************************

Provide connection to the existing storm sewer collection system at the point indicated on the drawings in another part of this RFP.  Confirm that the existing outfall has adequate capacity to receive the additional stormwater flow generated by the project.

[Provide vehicle wash areas.]

G303001 STORM SEWER PIPING

********************************************************************************************************** 
NOTE:  Indicate any preferences of the utility provider in this section.  Include information such as pipe materials, pipe linings, and corrosion protection. 
**********************************************************************************************************

The following materials for storm sewer piping are not allowed: [PVC] [ductile iron] [reinforced concrete pipe] [corrugated steel] [corrugated aluminum] [polyethylene (PE)] [ polypropylene (PP)] [_____].

[Due to corrosive soil conditions, storm sewer piping materials are required to be [polyvinyl chloride (PVC)] [,] [reinforced concrete] [,] [polyethylene (PE)] [or] [polypropylene (PP)].]

G303002 STORM SEWER STRUCTURES

********************************************************************************************************** 
NOTE:  Indicate any preferences of the utility provider in this section.  Include information such as types of storm structures and materials. **********************************************************************************************************

********************************************************************************************************** 
NOTE:  Stormwater lift stations are rarely used.  **********************************************************************************************************

G303004 CULVERTS

********************************************************************************************************** 
NOTE:  Indicate any preferences of the utility provider in this section.  Include information such as pipe materials, pipe linings, and corrosion protection. 
**********************************************************************************************************

The following materials for culvert piping are not allowed: [PVC] [ductile iron] [reinforced concrete pipe] [corrugated steel] [corrugated aluminum] [polyethylene (PE)] [polypropylene (PP)] [_____].

[Due to corrosive soil conditions, storm sewer piping materials are required to be [polyvinyl chloride (PVC)] [,] [reinforced concrete] [,] [polyethylene (PE)] [or] [polypropylene (PP)].]

G303005 HEADWALLS

G303006 EROSION & SEDIMENT CONTROL MEASURES

********************************************************************************************************** 
NOTE:  Coordinate with the ESR and PTS Sections G103011, "Temporary Erosion & Sediment Control".
**********************************************************************************************************

G303007 STORM WATER MANAGEMENT

********************************************************************************************************** 
NOTE:  For projects that require storm water management delete the last bracketed sentence.  If storm water management is not required choose the last bracketed sentence below and delete all preceding bracketed paragraphs.
**********************************************************************************************************

********************************************************************************************************** 
NOTE: LID data is required to comply with DoD policy on implementation of storm water requirements under EISA Section 438 and to prepare annual reports to the Assistant Secretary of Navy.  The NAVFAC Low Impact Development (LID) Data Card and eProjects "LID Information" tab are used as the NAVFAC tool for documenting LID data and annual reporting for both EISA Section 438 and Navy LID Policy.  The Government's PM, DM or Civil Engineer will review the NAVFAC Low Impact Development (LID) Data Card submitted by the Designer of Record (DOR) and document on the eProjects LID Information tab. The Government's Civil Engineer is responsible for storing the DOR's calculations in the project file.
**********************************************************************************************************

********************************************************************************************************** 
NOTE:  For projects near airfields, storm water management facilities such as retention/detention ponds may not be allowed due to bird hazards.
**********************************************************************************************************

********************************************************************************************************** 
NOTE:  Each LID feature has unique requirements that may (or may not) be suitable for your location and should be individually selected below.
**********************************************************************************************************

[Provide stormwater management that complies with [state stormwater regulations, ][the utility provider's requirements, ]UFC 3-201-01 Civil Engineering, UFC 3-210-10 Low Impact Development, FC 1-300-09N Navy and Marine Corps Design Procedures; whichever is more stringent.  [Provide Low Impact Development (LID) features in accordance with UFC 3-210-10 Low Impact Development.  The following LID features may be used: [bioretention, ][dry wells, ][filter/buffer strips, ][grassed swales, ][bioretention swales, ][wet swales, ][rain barrels, ][cisterns, ][infiltration trenches, ][rain gardens, ][permeable pavement or pavers, ][___, ]and [tree box filters].[ The use of [bioretention, ][dry wells, ][filter/buffer strips, ][grassed swales, ][bioretention swales, ][wet swales, ][rain barrels, ][cisterns, ][infiltration trenches, ][rain gardens, ][permeable pavement/pavers, ] [___, ]and [tree box filters] are not allowed for this project.

For Navy and Marine Corps projects, use FC 1-300-09N Navy and Marine Corps Design Proceduresto comply with Navy LID Policy (commonly referred to as the Penn Memo).  Navy LID policy sets a goal of no net increase in stormwater and sediment or nutrient loading from major renovation projects and construction projects.  Major renovation projects are defined as having a storm water component and exceeding $5 million and major construction projects are defined as exceeding $750,000.  If LID is not implemented to the Maximum Extent Technically Feasible (METF), as defined in UFC 3-210-10, a waiver request must be approved by the Regional Engineer.  Coordinate waiver review and approval with the Civil Technical Discipline Coordinator (TDC).

Projects with a footprint exceeding 5,000 SF or exceeding the dollar values above must be documented on the NAVFAC Low Impact Development (LID) Data Card and submitted to the Government's Civil Engineer for review and approval.

The NAVFAC Low Impact Development (LID) Waiver Form and Low Impact Development (LID) Data Card can be found at: https://www.wbdg.org/ffc/dod/tri-services-sustainability-program/tracking-reporting .

The Contractor must obtain [State Stormwater Management]  [and ____] regulatory permits required for the proposed work from the [EPA][State] [Installation Environmental Stormwater Program Manager].  Coordinate reports, submittals, and permit applications through the Contracting Officer.]

[Storm water management is not required for this project.]