*************************************************************************** 
NAVFAC                                                 PTS-B20 (June 2023)
                                             ------------------------------
Preparing Activity: NAVFAC                 SUPERSEDING PTS-B20 (September 2022)
 
PERFORMANCE TECHNICAL SPECIFICATION
 
***************************************************************************

SECTION B20

EXTERIOR ENCLOSURE
06/23

*************************************************************************** 
NOTE:  This section is intended to be used as a guide and contains requirements that are common to many different types of facilities; however, not all requirements and equipment items will be applicable to all projects. In addition, there may be special requirements for a particular project that are not addressed at all.  The RFP preparer may have to incorporate additional information to address these special requirements in this PTS and the corresponding RFP Part 3 ESR.  If the RFP preparer chooses to delete building elements that are not required for the project, do not change the remaining Uniformat paragraph designations (A102001).  Uniformat designations are unique to the products they are assigned to.  However, the subparagraph numerical extensions (example - 1.2 or a,b,c) of the Uniformat designations may change if subparagraphs are deleted.

This guide specification is formatted utilizing Uniformat II, an industry recognized standard, ASTM E 1557.  When the RFP preparer chooses to add a paragraph that does not apply to an existing building element already included in the specification, refer to the Uniformat/WBS located on the NAVFAC Design-Build Website for a listing of Uniformat II designations and definitions.

NOTE: The RFP preparer may view or hide the criteria notes in this PTS section by modifying the WORD preferences for "Hidden text".  To view the criteria notes, choose "File" then "Option".  Click "Display" then check the "Hidden text" box under "Always show these formatting marks on the screen".  In the same section, check the box for "Print hidden text" under "Printing options" to print the criteria notes.
***************************************************************************

*************************************************************************** 
NOTE:  This section consists of the exterior facing of the facility, which includes all vertical and horizontal exterior closure features excluding the roof. (See Section B30, Roofing). Load bearing exterior walls are included here and not in Section B10, Superstructure. Structural frame elements at exterior such as columns and beams are included in Section B10, Superstructure, with only the applied exterior finishes (e.g., paint, stucco) being included here. Finishes to the inside face of walls which are not an integral part of the wall construction are included on Section C30, Interior Finishes.
***************************************************************************

*************************************************************************** 
NOTE:  The following Table of Contents is for navigation purposes within the document.

TABLE OF CONTENTS

B20  GENERAL
B20  1.1  DESIGN GUIDANCE
B20  1.2  PERFORMANCE VERIFICATION AND ACCEPTANCE TESTING
B2010  EXTERIOR WALLS
B201005  EXTERIOR LOUVERS & SCREENS
B201006  HANDRAILS
B201006  1.1  HANDRAILS
B201009  EXTERIOR PAINTING AND SPECIAL COATINGS
B201009  1.1  GENERAL REQUIREMENTS
B201009  1.2  ADDITIONAL EXTERIOR PAINT AND COATING SYSTEM REQUIREMENT
B201010  EXTERIOR JOINT SEALANT
B2030  EXTERIOR DOORS
B203001  SOLID DOORS
B203001  1.1  STEEL DOORS
B203006  EXTERIOR BLAST DOORS
B203006  1.1  CUSTOM FABRICATED STEEL BLAST DOORS
B203006  1.2  CUSTOM FABRICATED STEEL BLAST DOOR HARDWARE
B203006  1.3  CUSTOM FABRICATED STEEL BLAST DOOR LOCKS
***************************************************************************

B20 GENERAL

RFP Part 3 including the Engineering System Requirements (ESR) provide project specific requirements.  The RFP Part 4, Performance Technical Sections (PTS) provide generalized technical requirements that apply to multiple facility types and include more requirements than are applicable to any one project. Therefore, only the RFP Part 4 requirements that apply to the project and further define the RFP Part 3 project specific requirements are required.

B20 1.1 DESIGN GUIDANCE

Provide the design and installation in accordance with the following references.  This Performance Technical Specification (PTS) adds clarification to the fundamental requirements contained in the following Government Standards.  The general requirements of this PTS section are located in PTS Section Z10, General Performance Technical Specification.

Industry standards, codes, and Government standards referenced in the section text that are not found in the Unified Master Reference List (UMRL)  in the Federal Facility Criteria (FFC)  at the Whole Building Design Guide (WBDG)  website, are listed below for basic designation identification.  Comply with the required and advisory portions of the current edition of the referenced standard at the time of contract award.

*************************************************************************** 
NOTE: Edit the following list of industry and Government standards to coordinate with the section text additions and deletions.  List all industry and Government standards in the following two paragraphs that are indicated in the section text that are not listed in the UMRL.
***************************************************************************

B20 1.2 PERFORMANCE VERIFICATION AND ACCEPTANCE TESTING

Provide verification of satisfactory exterior enclosure system performance via Performance Verification Testing, and by field inspection as detailed in this section of the RFP.  Provide special tests and special inspections in accordance with Part 2 Section 01 45 00, Quality Control.  The cost of all testing is included in the Contract.

B20 1.2.1 Air Barrier Field Sample

Designate a portion of the project that reveals the various edge, seam, transition, and penetration conditions that the air barrier is exposed to.  Determine this location with the Contracting Officer and obtain approval of the sealing methods employed on the project from the air barrier Manufacturer.  Leave sample area exposed to view as long as practical to serve as a construction standard and comparison of future air barrier construction on the project.  Before construction covers the sample area, provide detailed photographs of the air barrier details for future reference.

B20 1.2.2 Air Barrier Performance

Provide air barrier inspection on all projects and air barrier performance testing when required in RFP Part 3, Section B20.

B20 1.2.2.1 Air Barrier Inspection

Coordinate all subcontractors that provide part of the air barrier construction to provide an air tight barrier. Review the air barrier prior to being covered by subsequent construction to confirm that the air barrier complies with the following requirements;

a.	Prior to applying an air barrier, confirm that the substrate complies with conditions required by the applied air barrier material manufacturer.

b.	Air barrier must create a continuous barrier, without gaps, "fish mouths", holes, unsealed seams, or unsealed penetrations.

c.	Air barrier components are compatible and capable of being permanently connected to form an air tight barrier.

d.	Construction of the air barrier complies with air barrier design as indicated in the Basis of Design and exterior enclosure barrier drawings.

e.	Air barrier is installed in accordance with manufacturer's standard details available on the Air Barrier Association of America (ABAA) website named "Air Barrier Materials, Components, Assemblies & Systems" and found at the following web link; http://www.airbarrier.org/materials/assemblies_e.php

B20 1.2.3 Thermal Envelope Performance Testing (Infrared Thermography)

Where required in RFP Part 3  or B20 1.2.3.2 Air Barrier Performance Testing, provide infrared thermal testing and repair as follows (coordinate with air barrier testing):

a.	Test the building envelope using Infrared Thermography technology. Complete thermography testing in accordance with the requirements of ASTM E1186 and ISO 6781. The Contracting Officer will witness the testing. Testing must occur just before the building air tightness test. Testing must also occur during the air tightness test so that areas of building air leaks are detected. If the building air tightness test is failed, repeat thermographic testing just before and during subsequent air tightness tests until the air tightness test is successful.

b.	Thermographer Qualifications: the lead thermographer must have qualifications meeting requirements in UFGS Section 01 91 19.

c.	Thermography Test Procedures: Submit detailed test procedures indicating the test apparatus, the test methods and procedures, and the analysis methods to be employed not later than 60 days after Notice to Proceed.

d.	Thermography Test Report: Provide a report. The report must include thermographs in color and a color temperature scale to define the temperature indicated by the various colors. The report must identify the high temperature reading, the outdoor air temperature, the building indoor air temperature, and the wind speed and direction. The report must note any areas of compromise in the building envelope, and must note all actions required and taken to correct those areas.

e.	Final Test: Final thermography test report must demonstrate the problem areas have been corrected. Submit the complete test and analysis for review and approval.

B20 1.2.4 Air Barrier Performance Testing

Provide air barrier testing and repair as follows (coordinate with infrared thermal testing):

a.	Provide a testing plan as a part of the Commissioning Plan and notify the Contracting Officer 7 working days before the testing will take place. Do not test the building until verifying that the continuous air barrier is in place and installed without failures in accordance with installation instructions so that repairs to the continuous air barrier, if needed to comply with the required air leakage rate, can be done in a timely manner.

Also coordinate building access during the test with the Contracting Officer.  Perform pretest inspection with all parties involved in the test and possible repairs of the building enclosure.  Record pretest conditions and utilize pictures to assist in the documentation.

b.	Designer of Record (DOR) must utilize UFGS Section 01 91 19, Building Enclosure Commissioning,and Contractor must perform testing as described in that specification.  Where conflicts exist between the UFGS Section 01 19 19 and this performance specification, UFGS Section 01 91 19 will govern. The air leak flow rate must not exceed 0.25 CFM at 75 Pa per square foot (0.076 cmm 75 Pa per square meter) of building enclosure area including roof or ceiling, walls and floor as provided by the DOR.

Method 1: This test consists of measuring the flow rates required to establish 12 positive and 12 negative building pressures from at least 25 Pa to at least 50 Pa. Take at least 12 bias pressure readings across the building enclosure averaged over 5 seconds each before and after the test. None of these readings must exceed 30% of the minimum test pressure.

Method 2: this test consists of measuring the flow rates required to establish 12 positive building pressures from at least 50 Pa to at least 75 Pa. Take at least 12 bias pressure readings across the building enclosure averaged over 5 seconds each before and after the test. None of these readings must exceed 20% of the minimum test pressure.

The test results must be either pass or fail. Provide the theoretical size of the opening that leaks the same amount as the building enclosure at 75 Pa, to facilitate the search for leaks and repair of the exterior enclosure.

c.	Provide infrared thermography to determine air leakage paths if facility fails to retain the required air pressure in the test above.  Utilize infrared cameras with a resolution of 0.1 degree C or better.

Perform infrared thermography in accordance with ISO 6781:1983 and     American Society for Testing and Materials (ASTM) C1060 and B20 1.2.4 Thermal Envelope Performance Testing (Infrared Thermography). Determine air leakage pathways in accordance with ASTM E1186 Standard Practices for Air Leakage Site Detection in Building Envelopes and Air Barrier Systems, and perform corrective work as necessary to achieve the whole building air leakage rate specified.

Modify construction to stop identified air leakage until target is reached.  Correct air path leaks at the source of the leak, do not use sealant to close air leakage paths that are required to be opened for maintenance of the facility such as fixtures, switches covers, receptacle covers, access doors, etc.

d.	Seal air leaks in the following order of priority:

1.	Top of the building.  These include attics, roof/wall intersections, penthouse doors and walls, HVAC equipment.

2.	Bottom of the building.  These include ground floor access doors and inspection hatches, exhaust and air intake vents, service penetrations of enclosure, crawl spaces.

3.	Vertical shafts.  These include gasket stairwell fire doors, fire hose cabinets and recessed toilet accessories connected to vertical shaft, vertical and horizontal utility penetrations in service rooms, elevator rooms and shafts.

4.	Exterior walls.  These include weather strip doors and windows, exhaust fans and ducts, service penetrations, electrical receptacles, wall base.

B20 1.2.5 Required Records for Concrete Wall Panels

a.	Cast-in-place - Submit to DOR mandatory batch ticket information as ASTM C 94 for each load of ready-mixed concrete.

b.	Submit to DOR commercial testing results in accordance with PCI MNL-117 and as required in paragraph entitled "Sampling and Testing for Precast"

*************************************************************************** 
NOTE:  The test method of ASTM E 331 is that of determining resistance of the curtain wall to water penetration under uniform static air pressure difference.  When testing under dynamic conditions is required, AAMA Specification should be referenced.  The availability of facilities for conducting dynamic testing is very limited and should be checked before specifying this type of test.
***************************************************************************

B2010 EXTERIOR WALLS

Provide exterior wall construction that consists of exterior skin system of non-structural outside face elements with rain-screen back-up wall systems that include; flashing (embedded, exposed, and thru-wall), a water resistive barrier, moisture barrier/ vapor retarder (if required), air barrier, and insulation systems with interior skin system materials to provide a protective finish on the inside face of exterior walls. Provide all components necessary for a shingled water resistive barrier to direct water that would penetrate the wall to be directed to the outside of the wall.  Provide exterior enclosure components and barriers in accordance with UFC 3-101-01, Architecture.

Design all work to comply with UFC 3-101-01, Architecture, and UFC 3-301-01, Structural Engineering, and the following requirements:

a.	Vapor Pressure and Hygrothermal Analysis - Perform a job specific vapor pressure and hygrothermal analysis in accordance with UFC 3-101-01, Architecture.  The conclusion of the analysis must indicate if a moisture barrier/ vapor retarder is required, the appropriate locations of needed moisture barrier/ vapor retarder, and anticipated dew-point locations in the exterior enclosure during different critical times of the year.

b.	Wind Loads - Provide wind load calculations for exterior cladding in accordance with UFC 1-200-01 and UFC 3-301-01 with comparative analysis of the cladding system to be provided.

c.	Water Penetration - No water penetration must occur at a pressure of 8 psf (39 Kg/m2) of fixed area when tested in accordance with ASTM E 331.

d.	Insulating Value – Comply with UFC 3-101-01, Architecture, for the     American Society of Heating, Refrigerating, and Air-Conditioning Engineers (ASHRAE) 90.1 standards to determine the minimum insulating value of the complete wall system.

B201005 EXTERIOR LOUVERS & SCREENS

Provide louvers as shown on the definitive drawings.

B201006 HANDRAILS

B201006 1.1 HANDRAILS

Design handrails and anchorage connections to resist loads in accordance with IBC.  Provide steel and aluminum materials in accordance with NAAMM Pipe Railing Systems Manual, with the same size handrail and vertical post.  Provide series 300 stainless steel pipe collars.  Factory coat all metal railings, except ornamental metals such as brass, bronze, and nickel-silver, with a high performance coating in accordance with AAMA 2605 for aluminum with a minimum coating thickness of 1.2 mils unless otherwise noted.      For steel handrails provide finish coating in accordance with UFGS 09 96 00, High Performance Coatings.

B201006 1.1.1 Fiber  Reinforced Plastic (FRP) Handrails

*************************************************************************** 
 NOTE:  FRP handrails are only an option for mechanical mezzanine, utility or like construction only.
 ***************************************************************************

Provide FRP handrails in structural shapes manufactured by the pultrusion process with qualities, quantities, properties, arrangements and dimensions as necessary to meet the design requirements in accordance with ASCE 7,29 Code of Federal Regulations (CFR) 1910.23, National Fire Protection Association (NFPA) 101.  Provide integral UV inhibitors within the resin, synthetic surfacing veil to help produce a resin rich surface, and UV resistant coating for outdoor exposures.

B201006 1.1.2 Steel Handrails

Provide steel handrails, including inserts in concrete, steel pipe conforming to ASTM A 53 or structural tubing conforming to ASTM A 500, Grade A or B of equivalent strength.  Steel railings must be of 1 1/2 inches (38 mm) nominal size.  Railings must be hot-dip galvanized, shop primed shop painted for exterior applications.

B201009 EXTERIOR PAINTING AND SPECIAL COATINGS

Apply coatings directly to all non-prefinished surfaces of the exterior construction. Comply with Master Painters Institute requirements for surface degradation analysis, surface preparation, paint and coating selection, paint application restrictions for substrate materials, and paint application.

B201009 1.1 GENERAL REQUIREMENTS

Painting practices must comply with applicable federal, state and local laws enacted to insure compliance with Federal Clean Air Standards.  Apply coating materials in accordance with     Society for Protective Coatings (SSPC) PA 1.  SSPC PA 1 methods are applicable to all substrates.

Provide all paint in accordance with the Master Painter Institute (MPI) standards for the exterior architectural surface being finished.  The current MPI, "Approved Product List" which lists paint by brand, label, product name and product code as of the date of contract award, will be used to determine compliance with the submittal requirements of this specification.  The Contractor may choose to use a more current MPI "Approved Product List"; however, only one list may be used for the entire contract. All coats on a particular substrate, or a paint system, must be from a single manufacturer.  No variation from the MPI Approved Products List is acceptable.

Select paint systems for the project in accordance with the MPI Architectural Painting Decision Tree available on the Whole Building Design Guide.  Use this interactive MPI Decision Tree website to identify applicable paint system(s) for the project. The MPI Decision Tree identifies paint systems for each interior or exterior coated surface in "Normal" or "Aggressive" environmental conditions and generally lists the applicable paint systems in descending order of performance.  The paint system at the top of each substrate list generally indicates the highest performing acceptable coating system.

Choose the "Aggressive" environmental conditions in the MPI Decision Tree for exterior systems that are used in moist humid conditions, abrasive conditions, chemical exposure conditions, or within five miles proximity of the ocean or a body of water. Also use "Aggressive " environmental conditions in interior spaces that are exposed to in moist humid conditions, abrasive conditions, chemical exposure conditions, such as bathrooms, shower rooms, kitchens, chemical storage area, swimming pools, laundry, sanitary areas, commercial kitchens, industrial production areas, and hospital operating rooms provide paint systems that comply with the MPI Decision Tree "Aggressive" environmental conditions.

Comply with the following requirements when determining the appropriate paint or coating system from the MPI Decision Tree:

a.    Some of these paint systems are identified with a "NAVFAC Anchor".  This "NAVFAC Anchor" indicates the minimum performing system that NAVFAC will accept for that substrate and environmental conditions.

b.    When multiple "NAVFAC Anchors" are indicated on a certain substrate and environmental condition, provide the "NAVFAC Anchor" paint or coating system that is most appropriate for the facility use.

c.    If only one MPI Decision Tree choice is available for a certain substrate and environmental condition with no indicated NAVFAC preference, provide that sole option for NAVFAC projects.

d.    If the MPI Decision Tree provides multiple choices and no NAVFAC preference is denoted, refer to the Additional RFP Requirements below to determine level of performance.

e.    If the MPI Decision Tree does not identify all paint system applicable to the facility, utilize the MPI Architectural Painting, Exterior Systems Manual to identify other appropriate paint systems for the project. Utilize the "Premium Grade" systems and comply with all limitations stated in the MPI "Approved Product List" for each paint product.  Products having an MPI VOC Range E3 must be given preferential consideration over lower VOC Ranges.  Use higher performing paint systems unless the lower performing paint system can be justified based on a lifecycle cost to include surface preparation, application, disposal, environmental impact, and required recoating cycles.  Only use paint products that have been tested for MPI'S "DETAILED PERFORMANCE" or "EVALUATED PERFORMANCE ". Do not use products that have only been tested for "INTENDED USE".

f.    If an "Aggressive" environmental condition option is not available in the MPI Decision Tree for a certain substrate, use the "Normal" environmental condition option.

g.    Refer to the Additional Exterior Paint and Coating System Requirements below for further system requirements.

Paints and coatings must comply with Master Painters Institute Green Performance Standard GPS-1-12 which is available at the following website; http://www.specifygreen.com/EvrPerf/EnvironmentalPerformance.html .  Choose paints that provide performance, are environmentally friendly, and that conform to EPA or local environmental regulations, whichever requires the lowest VOC content.

B201009 1.1.1 MPI Gloss Levels

Gloss levels must comply with the MPI system of determining gloss as defined in the Evaluation sections of the MPI Manuals.  Utilize the performance characteristics of the paint gloss and sheen to categorize paint rather than manufacturers’ description of the product.  The MPI Gloss Levels are indicated by the notation G1, G2, G3, G4, G5, G6, or G7. Navy only uses MPI Gloss Levels G2, G3, G5, G6.

The MPI Decision Tree indicates a default gloss level for each paint system, however consider the appearance, anticipated conditions, and need for cleaning when establishing the final gloss level for each coated surface of the project. Comply with the following guidance in choosing the appropriate gloss level.

a.   Use G2 "Velvet-like" Flat for ceilings, residential walls away from human contact and low traffic areas.

b.   Use G3 "Eggshell-like" in high traffic areas for ceilings and walls, when human contact with the wall is limited, and for dark accent colors.

c.   Use G5 Semigloss for walls, doors and trim for high durability and clean ability and when a surface is expected to have routine human contact.

d.   Use G6 Gloss only in special situations such as for piping identification or special effects.

The MPI gloss and sheen standard values are in accordance with ASTM D523, and are as follows:

| Gloss Level Number | Gloss@60 Degrees | Sheen@85 Degrees |
| --- | --- | --- |
| Gloss Level 1 (G1) - Matte or Flat | Max.5 units | Max.10 units |
| Gloss Level 2 (G2) - "Velvet-like" Flat | Max. 10 units | 10-35 units |
| Gloss Level 3 (G3) - "Eggshell-like" | Max. 10-25 units | 10-35 units |
| Gloss Level 4 (G4) - "Satin-like" | Max. 20-35 units | Min. 35 units |
| Gloss Level 5 (G5) - Semi-Gloss | 35-70 units |  |
| Gloss Level 6 (G6) - Gloss | 70-85 units |  |
| Gloss Level 7 (G7) - High Gloss | More than 85 units |  |

B201009 1.1.2 MPI System Designations and Table Abbreviations

The MPI coating system number description is found in either the MPI Architectural Painting Specification Manualor the Maintenance Repainting Manualand defined as an exterior system

a.	EXT - MPI short-term designation for an exterior coating system on a new surface.

b.	REX - the MPI short term designation for an exterior coating system used in repainting projects or over existing coating systems.

c.	DSD - the MPI short-term designation for Degree of Surface Degradation as defined in the Assessment sections in the MPI Maintenance Repainting Manual.  Degree of Surface Degradation designates the MPI Standard for description and appearance of existing condition of surfaces to be painted. This DSD classification is used to determine the proper surface preparation necessary for painting.

B201009 1.1.3 Surface Preparation

Comply with the "Exterior Surface Preparation" section of the MPI Architectural Painting Specification Manual,or the Exterior Surface Preparation” section of the MPI Maintenance Repainting Manual. All suggestive language such as "may" or "should" are deleted from the standard and "must" inserted in its place. Suggestive language such as "recommended" or "advisable" is deleted from the standard and "require" or "required" inserted in its place. The results of these wording substitutions change this document to required procedures. For surface preparation, determine a MPI DSD Assessment of each surface and comply with the MPI Surface Preparation Requirements relating to the assessments.  Not-withstanding MPI requirements, clean exterior ferrous metal that is exposed to weather conditions (wind, precipitation, solar degradation, and humidity) to a SSPC SP 10 level (near white).

Remove dirt, splinters, loose particles, grease, oil, and other foreign matter and substances deleterious to coating performance as specified for each substrate before application of paint or surface treatments.  For existing buildings, use MPI Maintenance Repainting Manual to determine the coatings that need to be removed.  Remove deteriorated or loose coatings before repainting begins.  Remove oil and grease prior to mechanical cleaning.  Program cleaning so that dust and other contaminants will not fall on wet, newly painted surfaces.  Spot-prime exposed ferrous metals such as nail heads on or in contact with surfaces to be painted with water-thinned paints with a suitable corrosion-inhibitive primer capable of preventing flash rusting and compatible with the coating specified for the adjacent areas.

B201009 1.2 ADDITIONAL EXTERIOR PAINT AND COATING SYSTEM REQUIREMENTS

In addition to the MPI Decision Tree, comply with the following paint system requirements:

B201009 1.2.1 Pavement Coatings

a. EXT 3.2 Concrete Horizontal Surfaces

Normal/ Aggressive Condition; Pigmented;

Provide road and parking lot pavement marking in accordance with UFGS Section 32 17 23, Pavement Markings.

b. EXT 10.2 Bituminous Coated Surfaces

Normal/ Aggressive Condition; Pigmented;

Provide road and parking lot pavement marking in accordance with UFGS Section 32 17 23, Pavement Markings.

B201009 1.2.2 Hot Metal Surfaces (including smokestacks),

a. EXT 5.2 Hot Metal, Up to 205 degrees C 400 degrees F

Normal/ Aggressive Condition; Pigmented

(1) EXT 5.2A - Heat Resistant Enamel

Primer:     Intermediate/ Topcoat:

MPI 21      Surface Preparation and numbers of coats in accordance with manufacturers' instructions.

b. EXT 5.2 Hot Metal (Ferrous), Up to 400 degree C, 750 degree F

Normal/ Aggressive Condition; Pigmented;

(1) 5.2C - Heat resistant - inorganic zinc coating

Primer:     Intermediate/ Topcoat:

MPI 19      Surface Preparation and numbers of coats in accordance with manufacturers' instructions.

(2) 5.2B - Heat resistant - aluminum finish enamel

Primer:     Intermediate/ Topcoat:

MPI 2       Surface Preparation and numbers of coats in accordance with manufacturers' instructions.

c. EXT 5.2 Hot Metal (Non-Ferrous), Up to 593 degree C, 1100 degree F

Normal/ Aggressive Condition; Pigmented

(1) 5.2D - Heat Resistant Coating

New and existing surfaces cleaned bare to SSPC SP 10/NACE No. 2

Primer:     Intermediate/ Topcoat:

MPI 22      Surface Preparation and numbers of coats in accordance with manufacturers' instructions.

B201010 EXTERIOR JOINT SEALANT

Provide sealant joint design, priming, tooling, masking, cleaning and application in accordance with the general requirements of Sealants: A Professionals' Guidefrom the Sealant, Waterproofing & Restoration Institute (SWRI).  All sealant must conform to ASTM C 920.

Joints must include proper backing material for sealant support during application, control of sealant depth, and to act as a bond breaker.  Use filler boards, backer rods and bond breaker tapes.   Provide priming unless specifically not recommended by the sealant manufacturer.    Applied sealant must be tooled.  Tooling must not compact sealant too less than the minimum sealant thickness required.  Mask adjacent surfaces to control sealant boundaries during sealant application.

*************************************************************************** 
NOTE:  To comply with minimum antiterrorism (AT) requirements, specify in the project program the options for AAMA HC-60 and 90 psf (439 Kg/m2) below, when facility personnel density is greater than one person per 430 square feet (40 square meters) and minimum AT standoff distances are met.  This does not include guard type facilities, single and duplex detached family housing.  Those requirements are specified in UFC 4-010-01, DoD Minimum Antiterrorism Standards for Buildings.
***************************************************************************

*************************************************************************** 
NOTE:  If the editor makes adjustments in the minimum residential AAMA LC-25 (38 psf or 185 Kg/m2) or commercial AAMA HC-40 (60 psf - 293 Kg/m2) or HC-60 (90 psf - 439 Kg/m2) windows, adjust the minimum wind pressure to correspond to the modified window performance.  Refer to AAMA 101/I.S.2 to identify wind pressures that correspond to the modified AAMA window chosen.
***************************************************************************

B2030 EXTERIOR DOORS

Exterior doors must be high security fabricated steel doors as shown and detailed on the definitive drawings.

B203001 SOLID DOORS

B203001 1.1 STEEL DOORS

Hardward must be provided as detailed on the definitive drawings.

B203001 1.1.1 Steel Doors

Exterior steel doors must be high security fabricated steel doors as shown and detailed on the definitive drawings.

B203001 1.1.2 Finishes

a.	Exterior Doors, Factory-Primed and Field Painted Finish – Doors and frames must be factory primed with a rust inhibitive coating as specified in ANSI/SDI A250.8.

*************************************************************************** 
NOTE:  NAGDM 102 designates doors as follows:

Residential.  Intended for use in residential garage, normally operated less than 1,500 cycles per year.

Commercial.  Intended for vehicular use at entrances of commercial buildings such as loading docks and service stations, normally operated less than 5,000 cycles per year.

Industrial.  Intended for vehicular use at entrances of parking garages, factories, and manufacturing plants, normally operated in excess of 5,000 cycles per year.

If profile is indicated and there is a requirement for matching, add, "Profile of panels shall match profile indicated."
***************************************************************************

B203001 1.2 FIBERGLASS REINFORCED PLASTIC (FRP) DOORS

Hardware preparation must be in accordance with ANSI/BHMA A156.115.  Doors must be hung in accordance with ASTM E2112.

B203006 EXTERIOR BLAST DOORS

B203006 1.1 CUSTOM FABRICATED STEEL BLAST DOORS

Exterior doors shall be high security fabricated steel doors as shown and detailed on the definitive drawings.

B203006 1.2 CUSTOM FABRICASTED STEEL BLAST DOOR HARDWARE

Exterior door hardware shall be as shown and detailed on the definitive drawings.

B203006 1.3 CUSTOM FABRICASTED STEEL BLAST DOOR LOCKS

Exterior door hardware shall be high security locks and latches as shown and detailed on the definitive drawings.

-- End of Section –-

B203006 BLAST RESISTANT DOORS

Provide blast resistant doors as required by Part 3 of the RFP in accordance with UFC 4-010-01, DoD Minimum Antiterrorism Standards for Buildings.