6. ENGINEERING SYSTEMS REQUIREMENTS

D50 ELECTRICAL

********************************************************************************************************** 
SYSTEMS REQUIREMENTS
ELECTRICAL TEMPLATE 12/08
 
Instructions for using this template: There are template files for each UNIFORMAT Level 2 Group Elements. This template is for Group Element D50-ELECTRICAL. Text such as this is hidden text that will not print when the hidden text box in "Print/Options" is un-checked.

The Electrical Designer must edit this template for the requirements of the project and wherever brackets [ ] appear. The Electrical Designer shall use UFC 3-500-10N when determining electrical system requirements. 
 
It is acceptable to place all required information in the main element (such as D5010) and delete the sub-elements provided in this template.
 
The SYSTEMS REQUIREMENTS are intended to define items that are required throughout the facility or on a system wide basis that is common to several rooms. Room-specific requirements are defined in the ROOM REQUIREMENTS section. Coordinate with the lead programmer for ROOM REQUIREMENTS. Delete all building elements that are not required for the project. If additional elements or sub-elements are required for the project that do not appear in the template, refer to the NIST UNIFORMAT II publication for additional building element numbers and descriptions. The Uniformat II Work Breakdown Structure can be found at www.wbdg.org/ndbm/ . Coordinate with the PERFORMANCE TECHNICAL SPECIFICATION SECTION D50 (Section D50) to ensure that performance requirements are provided for all of the Building Elements listed here and that paragraph numbering matches.
 
There may be rare occasions when prescriptive specifications may either be edited and included in Part 5 of the RFP or required in Section D50 to be edited by the Contractor’s Designer of Record.    In both cases, the Engineering Systems Requirements (ESR) must include references to these documents.
**********************************************************************************************************

SYSTEM DESCRIPTION
********************************************************************************************************** 
NOTE: Address scope and ensure the system description clearly describes the existing systems and designated connection points as applicable, and any other information needed for the contractor to understand the existing system and how the new project will connect to it.    
**********************************************************************************************************

[Demolish the existing [    ] system [and provide new [    ].]

Provide an interior electrical system consisting of [Service Entrance Wiring and Equipment,] [Distribution and Lighting Panelboards,] [Dry Type Transformers,] [Conduits,] [Feeder and Branch Circuits,] [Motor Control Equipment,] [Lighting and Branch Wiring,] [Communications, Security and Alarm Systems,] [Emergency Generator], [Emergency Lighting and Power,] [Grounding,] [Lightning Protection,] [400-Hertz Converters], [UPS,] [                ] including accessories and devices as necessary and required for a complete and usable system.    This section covers installations out to the building 5 foot (1.5 meter) line.

The interior distribution system shall consist of insulated conductors in conduit.

GENERAL SYSTEM REQUIREMENTS
Provide an Electrical System complete in place, tested and approved, as specified throughout this RFP, as needed for a complete, usable and proper installation. All equipment shall be installed per the criteria of PTS Section D50 and the manufacturer’s recommendations. Where the word "should" is used in the manufacturer’s recommendations, substitute the word "shall".

********************************************************************************************************** 
NOTE:    Requirements for Government Furnished Equipment (GFE) are provided in ESR E10, Equipment.
**********************************************************************************************************

D5010 ELECTRICAL SERVICE AND DISTRIBUTION

********************************************************************************************************** 
NOTE:    Typically, the scope of design build projects covered by this specification will limit the voltage in a facility to 480 volts maximum. All medium voltage work will generally be exterior to the facility and will be covered in ESR G40.
**********************************************************************************************************

D501001 MAIN TRANSFORMERS

Main transformer(s) are defined in Section G40, Site Electrical Utilities.

D501002 SERVICE ENTRANCE EQUIPMENT

All service into the facility shall be underground.

[Provide a [switchgear] [switchboard] [main distribution panel] as service equipment. [Provide each [switchgear] [switchboard] with digital metering.]

D501003 INTERIOR DISTRIBUTION TRANSFORMERS

[Provide dry type transformers to step down secondary voltages for general purpose outlets and other low voltage equipment.]

D501004 PANELBOARDS

[Provide distribution and branch circuit panelboards to serve loads as required.]

D501005 ENCLOSED CIRCUIT BREAKERS

[Provide enclosed circuit breakers for [          ]]

D501006 MOTOR CONTROL CENTERS

********************************************************************************************************** 
NOTE:    RFP writer shall thoroughly coordinate this section with the mechanical design requirements. Delete all paragraphs that do not apply.
**********************************************************************************************************

Provide [motor control centers] [individual motor starters with disconnect switches] [combination motor starters][variable speed drives] [reduced voltage controllers] [manual motor starters] for motor controls as required by mechanical equipment. Provide all circuits and connections for motor [    ].

D501090 OTHER SERVICE AND DISTRIBUTION

********************************************************************************************************** 
NOTE:    Determine if transient voltage surge suppressors (TVSS) will be required for switchgear, switchboards, or panelboards.
**********************************************************************************************************

[Provide transient voltage surge suppressors (TVSS) at the following locations [service entrance] [                  ]].

********************************************************************************************************** 
NOTE:    Busway is generally reserved for power systems that require constant rearrangement such as machine shops and will typically not be used. Delete when not required.
**********************************************************************************************************

[Provide a complete system of [feeder bus] [plug-in busway including bus plugs] to serve [                  ] systems.]

[Busway shall be copper.]

D5020 LIGHTING AND BRANCH WIRING

Provide electrical connections for all systems requiring electrical service.

Provide lighting and general purpose receptacles throughout all spaces as required.

********************************************************************************************************** 
NOTE:    Edit to identify project specific special outlets required. Include amp and voltage requirements as appropriate.
**********************************************************************************************************

Provide dedicated circuits and connections for the following special outlets: [            ].

D502001    BRANCH WIRING

All branch wiring shall be [insulated conductors in conduit] [non-metallic sheathed cable].

D502002 LIGHTING EQUIPMENT

[Provide a complete lighting system consisting of exit and emergency lighting and area lighting consisting of [fluorescent] [incandescent] [high intensity discharge] lighting including switches and automatic controls including [occupancy sensors][automatic lighting shutoff systems] [dimming systems].]

D5030 COMMUNICATIONS AND SECURITY

The Room Requirements Section identifies locations for communications and security systems and equipment, unless noted otherwise in the following sub-elements.

D503001 TELECOMMUNICATIONS SYSTEMS

********************************************************************************************************** 
NOTE:    Edit the following to meet the base and or activity requirements. Include Category 6 cable requirement here.    This coordinates with the latest guidance indicated in UFC 3-580-01 and will override the conflict in UFC 3-580-10 that required Category 5A cable.
**********************************************************************************************************

Provide a complete building entrance facility, backbone distribution system, and horizontal distribution system including, but not necessarily limited to, all [wiring,] [pathway systems,] [grounding,] [backboards,] [connector blocks,] [protectors for all copper service entrance pairs,] [patch panels,] [fiber optic distribution panels,] [terminators for all fiber optic cables,] [outlet boxes,] [telephone jacks,] [data jacks] [cover plates] and [                                ].

Provide Category 6 Unshielded Twisted Pair (UTP) copper cable for horizontal voice and data cables.

D503002 PUBLIC ADDRESS SYSTEMS

********************************************************************************************************** 
NOTE:    The Public Address System and the Intercommunications system may generally be combined into one system and utilize the telephone system and desktop phones for all communications. Coordinate and verify with user if this is a suitable system for mission accomplishment.
**********************************************************************************************************

[Provide a Public Address system with speakers in all [common spaces] [exterior speakers for outside activity spaces] [                ].

********************************************************************************************************** 
NOTE:    Include bracketed option when project involves hangar or large, open work spaces.
**********************************************************************************************************

[In [hangar] [          ] spaces, provide handset type microphone dedicated to speakers in the [hangar] [          ] space only. ]

********************************************************************************************************** 
NOTE:    Include the following option when project requires a mass notification system and combining the two systems is feasible.
**********************************************************************************************************

[Interface the Public Address System with the Mass Notification System.]

D503003 INTERCOMMUNICATIONS SYSTEMS

********************************************************************************************************** 
NOTE:    The Public Address System and the Intercommunications system may generally be combined into one and utilize the telephone system and desktop phones for all communications. Coordinate and verify with user if this is a suitable system for mission accomplishment. When project involves hangar space and maintenance shops, include separate Maintenance Control Intercom system.
**********************************************************************************************************

[Provide an Intercommunication System to allow two-way communications between all [office spaces], [locker rooms], [storage areas], [Department Heads], [Commanding Officer], [Executive Officer], [Officers Ready Rooms], [Maintenance Control Rooms], [Administration Offices and Maintenance Administration Offices], [            ].]

[Provide a separate stand-alone intercommunications system with individual two-way connections between the Maintenance Control Office and each shop space. This system shall be completely independent from the telephone system.]

D503004 TELEVISION SYSTEMS

********************************************************************************************************** 
NOTE:    CCTV for training is typically required in facilities where classrooms and training takes place.    Coordinate requirements with the using activity.    Delete this paragraph when not required. CCTV Systems are generally provided with empty raceways only.    If complete system is required, this section and PTS D50 will require extensive modifications.
**********************************************************************************************************

[Provide a CCTV system for training purposes including, but not necessarily limited to, cable supporting structures, including equipment racks, empty conduits with pull strings, junction boxes, outlet boxes, outlet connectors, and cover plates.]

********************************************************************************************************** 
NOTE:    Coordinate locations with the using activity and edit accordingly.
**********************************************************************************************************

[Provide [      ] CCTV outlets.]

********************************************************************************************************** 
NOTE:    Community Antenna Television Systems (CATV) are generally referred to as Cable TV.    Determine if there will be a CATV system that is not owned and maintained by the Government.
 
If the system will not be owned by the government, specify the requirements for empty raceways and outlet boxes to enable system installation by the commercial CATV supplier.
 
If the system will be owned by the government, specify a complete system.    Include backbone consisting of backboards/cabinets, wire, conduit, outlets and jacks in all offices.    Include jacks in other locations as required by the user.
**********************************************************************************************************

[Provide a CATV system consisting of empty raceways and outlet boxes to enable system installation by the commercial CATV supplier.]

[Provide a complete CATV system to be owned and maintained by the Government including all interior equipment required to provide high quality TV signals to all outlets with a return path for interactive television and cable modem access. System shall include, but is not necessarily limited to,    [headend amplifier,] amplifiers, splitters, combiners, line taps, cables, outlets, tilt compensators and all other parts, components, and equipment necessary to provide a complete and usable system. ]

********************************************************************************************************** 
NOTE:    Coordinate locations with the using activity and edit accordingly.
**********************************************************************************************************

[Provide    CATV outlets in [      ].]

********************************************************************************************************** 
NOTE:    Specify CATV testing method to ensure that the RFP is complete.
**********************************************************************************************************

Conduct CATV testing at each of the following points in the system:

********************************************************************************************************** 
NOTE: Use option for testing at each outlet instead of random sampling and at the furthest outlet when project includes only a small number of outlets.
**********************************************************************************************************

Furthest outlet from [each communications closet] [service entrance point of connection]
A random sampling of 25 percent of the [outlets [from each communication closet] [housing units] as designated by the Contracting Officer.
[At each outlet.]
[Head end] and [Distribution amplifier inputs and outputs.]

D503005 SECURITY SYSTEMS

********************************************************************************************************** 
NOTE:    For FY06 projects and beyond, NAVFAC's goal, is to fully integrate the design, procurement, installation and testing of ESS into Navy MCON design and construction contracts.    ESS supporting infrastructure will be included in the base construction contract and the procurement, installation, and testing will be included as an option.
 
ESS requirements vary from project to project and differ at each activity.    Installation of an ESS including designating protected areas/zones shall be indicated in the Project Program.    If an ESS is required, coordinate requirements with Project Manager and Base and Regional Security Personnel.
 
The following is provided for guidance only and should be edited accordingly to suit each project. ESS shall be fully coordinated and defined by the RFP writer and not left up to the design builder.
 
For Marine Corps projects, provide infrastructure support only.    Coordination with Commandant Marine Corps (CMC) is required.
**********************************************************************************************************

An Electronic Security System (ESS) is the integrated electronic system that encompasses one or more of the following subsystems; access control system (ACS), intrusion detection system (IDS), and closed circuit television (CCTV) systems for assessment of alarm conditions.

The ESS for this project shall consist of [an ACS] [and] [an IDS] [and] [a CCTV system for alarm assessment].

********************************************************************************************************** 
NOTE: If the ESS equipment will be provided by others, specify the requirements for empty raceways and outlet boxes to enable system installation by the ESS supplier.
**********************************************************************************************************

[Provide an ESS consisting of empty raceways with pull strings, outlet boxes, cover plates, and associated power outlets to enable system installation by the ESS supplier.]

********************************************************************************************************** 
NOTE: If the system will provided under this contract, specify a complete system that includes equipment and supporting infrastructure as required
**********************************************************************************************************

[Provide an electronic security system (ESS) including equipment and supporting infrastructure complete, tested, and operational.    ESS shall be compatible with the Installation’s central monitoring system and monitored [within the protected zone/area] [and] [at the Installation central monitoring station].

[Provide an ACS utilizing [credential devices] [coded devices] [and] [biometric devices] to monitor and control personnel movement through and within [protected areas][ the facility.] The ACS shall log and archive all transactions and alert authorities of unauthorized entry attempts. [ACS shall be interfaced with the CCTV system to archive unauthorized entry attempts and assist security personnel in the assessment of unauthorized entry attempts].]

[Provide and IDS to detect intruders or unauthorized personnel in protected areas/zones.    Provide point sensors on all windows, doors, and man passable openings.    Provide volumetric sensors within protected areas/zones to detect movement within protected areas/zones. System shall annunciate [, print,] and archive alarm conditions [within the facility] [and] [at central monitoring station].]

[Provide an [interior] [and] [exterior] CCTV system consisting of devices to provide visual assessment and digital archiving of alarm conditions.    Features shall include interface to ESS for control of camera call up to video monitors [, pan-tilt-zoom camera control,] and digital video archiving based on alarm event triggers.    Video archiving capacity shall be a minimum of [30] [    ] days.    [Integration shall provide means to associate archived alarm events with recorded video at the [      ] location(s).] ] ]

********************************************************************************************************** 
NOTE:    Protected distribution system (PDS) is used to protect the transmission of unencrypted classified information such as the Secret Internet Protocol Router Network (SIPRNET), and is required throughout many industrial and administration type facilities.    Determine if PDS will be required for the project.    Guidance for installations is covered in IA PUB-5239-22, Information Assurance Protected Distribution System (PDS) Guidebook, which is issued "For Official Use Only".    As this document is not intended for general distribution, include spaces or offices specifically requiring SIPRNET outlets based on user requirements and Project Program in the Room Requirements.
**********************************************************************************************************

[Provide a Protected Distribution System (PDS) with [      ] SIPRNET outlets.]

********************************************************************************************************** 
NOTE:    SCIF spaces must be distinctly identified in the Project Program and may also require connection to the ESS.    As a note, the term SCIF is very often "mistaken" to represent any space where classified documents or meetings occur.    SCIF spaces require very specific design and security requirements and are not representative of all secure offices or vaults.    RFP writer shall coordinate closely with Project Manager and architectural requirements to verify these requirements are applicable.    Delete when not required.    
**********************************************************************************************************

[The following [locations] [facilities] will be accredited SCIF spaces:

[            ], [            ].]

D503090 OTHER COMMUNICATIONS AND ALARM SYSTEMS

********************************************************************************************************** 
NOTE:    Mass Notification Systems are included in D40, Fire Protection.
**********************************************************************************************************

D5090 OTHER ELECTRICAL SERVICES

D509001 GENERAL CONSTRUCTION ITEMS (ELECTRICAL)

Provide General Construction Items (Electrical) including, but not necessarily limited to, all connections, fittings, boxes and associated equipment needed by this and other sections of this RFP as required for a complete and usable system.

Conduits, cable trays and busways that penetrate fire-rated walls, fire-rated partitions, or fire-rated floors shall be firestopped in accordance with Section C10, Interior Construction.

D509002 EMERGENCY LIGHTING AND POWER

[Provide power and wiring for emergency lights and exit lights throughout the facility.]

********************************************************************************************************** 
NOTE:    Edit the following as applicable when more than one emergency circuit is required. Identify circuits requiring emergency power such as FACP, ESS, etc. Include voltage and amp requirements.
**********************************************************************************************************

[Provide dedicated emergency power for the following loads:

[            ], [            ], [            ], [            ], [            ]]

********************************************************************************************************** 
NOTE:    Emergency generators should be limited to small packaged units based on scope of design build facilities addressed by this RFP. Large systems, paralleling schemes, etc. do not fall under the scope of the typical Design Build scenario. The RFP writer shall determine when and if generator power is required and edit accordingly. Do not size the generator but rather provide loads and voltages of dedicated equipment or circuits. Delete when not applicable.
**********************************************************************************************************

[Provide an emergency generator for power for the following loads and equipment: [          ], [            ], [            ]. The generator shall provide [              ] [minutes] [hours] [days] of emergency power.]

********************************************************************************************************** 
NOTE:    For projects in California requiring emergency diesel generators add the following.
**********************************************************************************************************

[Diesel fuel engines greater than 50 break horsepower (bhp) shall comply with the requirements of the Airborne Toxic Control Measure (ATCM) for Stationary Compression Ignition (CI) Engines (17CCR 93115) adopted by the California Air Resource Board (CARB).    For additional information go to http:www.sdapcd.org .]

********************************************************************************************************** 
NOTE:    UPS generally is not provided under construction but when required by the Activity should be provided for critical loads only and be limited to small (15-50 kVA) stand alone units based on scope of design build facilities addressed by this RFP. Large systems, paralleling schemes, redundant systems etc typically do not fall under the scope of the Design Build scenario. Small, individual, under desk type units are typically provided by the Government as collateral equipment and are not part of construction dollars. RFP writer shall determine when and if UPS power is required and edit accordingly. When complex systems are required, this section will require extensive modifications. Coordinate this section with the emergency generator section when both are required. Delete when not applicable.
**********************************************************************************************************

[Provide UPS power for the following critical loads and equipment:

[          ], [            ], [            ]. The UPS system shall provide [        ] minutes of emergency power to allow [startup and connection of the emergency generator] [an orderly shut down of the critical loads].]

D509003 GROUNDING SYSTEMS

Provide a complete grounding system for the facility electrical and telecommunications systems.

D509004    LIGHTNING PROTECTION

********************************************************************************************************** 
NOTE:    RFP writer shall make preliminary calculations and determine if a lightning protection system is required in accordance with NFPA 780 Appendix L "Lightning Risk Assessment".    Beginning in 2000, NFPA 780 changed its assessment procedure to use a "Lightning Flash Density Chart" in lieu of the "Lightning Frequency Isoceraunic Chart" used in previous versions, and includes recommendations of when to include a lightning protection system. Systems covered by this specification will generally be described in Chapter 4 of NFPA 780 "Protection of Ordinary Structures".    A "UL Lightning Protection Inspection Certificate certified to UL 96A" is now required in lieu of a “UL Master Label” when a system is provided. 
 
Include the bracketed option(s) when additional buildings or systems will require work in order to qualify for the Certificate.    Delete when not required.
**********************************************************************************************************

[Provide a complete lightning protection system with    a UL Lightning Protection Inspection Certificate certified to UL 96A, including, but not necessarily limited to, strike termination devices, conductors, ground terminals, interconnecting conductors, surge suppression devices, and other connectors and fittings required for a complete and usable system.]

[Work shall include necessary modifications to the existing lightning protection system on [          ] such that the entire system meets the UL Lightning Protection Inspection Certificate certified to UL 96A.] [Work shall include installation of a complete lightning protection system on [            ] such that the entire system meets the UL Lightning Protection Inspection Certificate certified to UL 96A.]

[Lightning Protection Systems shall not void the roof warranty.]

D509005 ELECTRIC HEATING

********************************************************************************************************** 
NOTE:    Electric heating will generally be sized and rated by the mechanical designers. Coordinate with mechanical and specifically point out any proposed large electric heating loads.
**********************************************************************************************************

[Provide power wiring and connections as required for all electric heating systems and equipment.]

D509006 ENERGY MANAGEMENT CONTROL SYSTEM

********************************************************************************************************** 
NOTE:    Energy management typically is covered in detail in the mechanical sections. RFP writer shall coordinate with mechanical and ensure that all power requirements are accounted for.
**********************************************************************************************************

[Provide power wiring and connections as required for all systems and equipment including [                                    ]. Coordinate connection requirements with switchgear and pad mounted transformer kWH metering.]

D509090 OTHER SPECIAL SYSTEMS AND DEVICES

********************************************************************************************************** 
NOTE:    400-Hertz power requirements shall be determined by the RFP writer based on user requirements. Aircraft power requirements have changed drastically recently (kVA and power quality requirements have generally increased) and values and requirements indicated in UFC 4-121-10N and UFC 3-555-01N may not be accurate. New aircraft may contain an individual power monitor that disconnects the aircraft from ground power when voltages exceed very specific requirements and the trend is to provide individual stand-alone units per each aircraft in lieu of the original distribution system as called for in the UFCs. Several new aircraft (E2C Hawkeye 2000 for instance) now also require two separate power sources due to the power monitor requirements. RFP writer shall include specific equipment requirements including number of units, kVA, requirements, etc.
 
Provide solid state frequency converters (UFGS Section 26 35 43) for most projects.    Only use 400 hertz motor generator sets (UFGS Section 26 32 26) when approved by the cognizant Facility Engineering Command (FEC).
**********************************************************************************************************

[Provide solid state frequency converter(s).]

[Provide a motor generator type frequency converter.]

[Provide 400 hertz power wiring and connections for the following loads and equipment:

[          ], [            ], [            ].

********************************************************************************************************** 
NOTE:    Provide descriptions below for any other special systems required in the project.
**********************************************************************************************************

[Provide power wiring and connections for the following special systems:

[            ], [            ].]

--End of Section--