*************************************************************************** 
NAVFAC                                                PTS-H50 (April 2008)
                                             -----------------------------
Preparing Activity: NAVFAC               SUPERSEDING PTS-H50 (March 2007)

PERFORMANCE TECHNICAL SPECIFICATION

***************************************************************************

SECTION H50

WATERFRONT UTILITIES
4/08

*************************************************************************** 
NOTE:  This section is intended to be used as a guide and contains requirements that are common to many different types of facilities; however, not all requirements and equipment items will be applicable to all projects.  In addition, there may be special requirements for a particular project that are not addressed at all.  The RFP preparer may have to incorporate additional information to address these special requirements in this PTS and corresponding Part 3 ESR.  If the RFP preparer chooses to delete elements that are not required for the project, do not change the remaining Uniformat paragraph designations (example - A102001). Uniformat designations are unique to the products they are assigned to. However, the subparagraph numerical extensions (example - 1.2 or a,b,c) of the Uniformat designations may change if subparagraphs are deleted.

This guide specification is formatted utilizing Uniformat II, an industry recognized standard, ASTM E 1557.  When the RFP preparer chooses to add a paragraph that does not apply to an existing building element already included in the specification, refer to the Uniformat/WBS located on the NAVFAC Design-Build Website for a listing of Uniformat II designations and definitions.

NOTE:  The RFP preparer may view or hide the criteria notes in this PTS section by modifying the WORD preferences in the document pull down menu for "Hidden text". To view the criteria notes choose "Tools, Options, and View," then check the "Hidden text" box, to print the criteria notes choose "Tools, Options, and Print," then check the "Hidden text" box.
***************************************************************************

*************************************************************************** 
NOTE:  The Table of Contents is intended for navigation purposes only for the RFP writer and should not show up in the printed document.

TABLE OF CONTENTS

H50 GENERAL
H50  1.1  NARRATIVE
H50  1.2  WATERFRONT UTILITIES DESIGN GUIDANCE
H50  1.3  QUALITY ASSURANCE
H50  1.4  DESIGN SUBMITTALS
H50  1.5  CONSTRUCTION SUBMITTALS
H5010  CIVIL/MECHANICAL UTILITIES
H5010  1.1  PIPE LOCATION
H5010  1.2  TEMPORARY REMOVAL AND REPLACEMENT
H501001  POTABLE WATER
H501001  1.1  PIPING
H501001  1.2  VALVES
H501001  1.3  BACKFLOW PREVENTERS
H501001  1.4  PRESSURE REGULATORS
H501001  1.5  UTILITY STATION PIPING AND OUTLET
H501002  SALTWATER
H501003  SANITARY SEWER
H501003  1.1  PIPING
H501003  1.2  VALVES
H501003  1.3  CAMLOCK HOSE COUPLING
H501004  BILGE AND OILY WASTE
H501004  1.1  PIPING
H501004  1.2  VALVES
H501004  1.3  CAMLOCK HOSE COUPLING
H501005  STEAM
H501006  COMPRESSED AIR
H501090  OTHER CIVIL/MECHANICAL UTILITIES
H501091  MISCELLANEOUS MATERIAL
H501091  1.1  PIPE GUARDRAILS
H501091  1.2  PIPE HANGERS AND SUPPORTS
H501091  1.3  HARDWARE
H501091  1.4  MISCELLANEOUS METAL
H5020   ELECTRICAL UTILITIES
H5020  1.1  DUCT/CONDUIT PLACEMENT
H502001  ELECTRICAL POWER DISTRIBUTION
H502001  1.1  ELECTRICAL POWER DISTRIBUTION
H502001  1.2  ELECTRICAL POWER OUTLET ASSEMBLIES
H502002  TELECOMMUNICATION
H502003  LIGHTING
H502004  LIGHTNING PROTECTION
H502005  ELECTRICAL POWER CABLE BOOMS FOR BERTHING OF SUBMARINES
H502090  OTHER ELECTRICAL UTILITIES
H5030  WATERFRONT FIRE PROTECTION
H503001  FIRE PROTECTION WATER
H503002  FIRE ALARM
***************************************************************************

H50 GENERAL

H50 1.1 NARRATIVE

This Section must be used in conjunction with all parts of the Design Build (D/B) Request for Proposal (RFP) to determine the full requirements of this solicitation.

This Section covers installations within the waterfront facility.  See PTS Sections G30, Site Civil/Mechanical Utilities, G40, Site Electrical Utilities, for continuation of systems beyond the five foot line.

H50 1.2 WATERFRONT UTILITIES DESIGN GUIDANCE

*************************************************************************** 
NOTE:  This Performance Technical Specification (PTS) has been developed to utilize certain UFGS sections for prescriptive requirements.  However, there may be rare occasions when additional prescriptive specifications may be identified by the Engineering Systems Requirements (ESR) to be edited by the Contractor's Designer of Record. If other UFGS sections or standards are to be referenced in this PTS section, list those not covered by the UMRL in the following two paragraphs.
 
If the product or system is new and not covered in the PTS, provide a new paragraph and heading.  If the product or system is presently covered in the PTS but is being changed by the reference to the UFGS, edit the PTS paragraphs to eliminate redundancy or conflicts.  In either case, identify the UFGS section in the products and materials (UNIFORMAT II/WBS level 4) text of the PTS as follows:
 
"Uniformat II/WBS Number – Paragraph Number Paragraph Heading
The Designer of Record shall utilize UFGS Section Number, "Section Title" for the project specification, and shall submit the edited specification section as a part of the design submittal for the project."
***************************************************************************

Provide the design and installation in accordance with the following references.  This Performance Technical Specification (PTS) adds clarification to the fundamental requirements contained in the following Government Standards.  The general requirements of this PTS Section are located in PTS Section Z10, General Performance Technical Specification.

H50 1.2.1 Government Standards

UNITED FACILITIES CRITERIA (UFC)

UFC 3-200-10N, Civil Engineering

UFC 3-600-10N, Fire Protection Engineering

UFC 4-150-02, Design: Dockside Utilities for Ship Service

UNIFIED FACILITIES GUIDE SPECIFICATIONS (UFGS)

UFGS Section 09 97 13.26, Coating of Steel Waterfront Structures

UFGS Section 26 05 33, Dockside Power Connection Stations

H50 1.3 QUALITY ASSURANCE

Qualifications, certifications, and Test Plans indicated herein shall be submitted 45 calendar days prior to the expected date of execution. Notify the Contracting Officer 14 calendar days prior to all testing. Submit test results within 7 calendar days of completion of testing.

The Designer of Record is responsible for approving the submittals listed below.

H50 1.3.1 Waterfront Civil/Mechanical Utilities

For waterfront civil/mechanical utilities quality assurance requirements, refer to applicable portion of the "Quality Assurance" paragraph in PTS Section G30, Site Civil/Mechanical Utilities.

H50 1.3.2 Waterfront Electrical Utilities

For waterfront electrical utilities quality assurance, refer to applicable portions of the "Quality Assurance" paragraph in PTS Section G40, Site Electrical Utilities.

H50 1.3.3 Waterfront Fire Protection

For waterfront fire protection quality assurance requirements, refer to applicable portion of the "Quality Assurance" paragraph in PTS Section D40, Fire Protection.

H50 1.4 DESIGN SUBMITTALS

Design submittals shall be in accordance with PTS Section Z10, General Performance Technical Specification, Section 01 33 10.05 20, Design Submittal Proceduresin Part 2, UFC 3-200-10N, Civil Engineering, UFC 3-400-10N, Mechanical Engineering, UFC 3-500-10N, Electrical Engineering, UFC 3-600-10N, Fire Protection Engineering, and UFC 4-150-02, Design: Dockside Utilities for Ship Services.

H50 1.5 CONSTRUCTION SUBMITTALS

The general requirements of this PTS Section are located in PTS Section Z10, General Performance Technical Specification.  Construction submittals shall be in accordance with Section 01 33 00.05 20, Construction Submittal Proceduresin Part 2.

If an OMSI manual is not a contract requirement, then provide product data for all equipment; and submit operation and maintenance data in accordance with Section 01 78 24.05 20, Facility Operation and Maintenance Support Informationin Part 2.

Provide certification that all adjustable protective device settings have been set in accordance with the coordination study for the as-built equipment and configuration.

H5010 CIVIL/MECHANICAL UTILITIES

H5010 1.1 PIPE LOCATION

Piping on deck with asphalt concrete pavement can be either placed underground, in a concrete trench or on a ledge outboard of the pier/wharf concrete curb/bullrail.  Piping on elevated concrete deck or concrete deck on-grade can be placed in a concrete trench or on a ledge outboard of the pier/wharf concrete curb/bullrail.  For utility trench requirements, refer to the "Utility Trenches" paragraph in PTS Section H10, Waterfront Structures.

H5010 1.2 TEMPORARY REMOVAL AND REPLACEMENT

Where necessary or as indicated on RFP drawings provided in Part 6, temporary removal and replacement of utilities and installation of interim facilities may be required to maintain services to existing facilities.  Temporary replacement facilities shall match the function and quality of existing facilities.

H501001 POTABLE WATER

Requirements for potable water on pier/wharf are provided below.  Additional requirements are provided in the "Potable Water Distribution" paragraph in PTS Section G30, Site Civil/Mechanical Utilities.

H501001 1.1 PIPING

Water service lines 100mm and smaller shall be brass pipe, ASTM B43, extra strong.  Fittings shall be brass or bronze, FS WW-P-460, 120 psi (825 kPa) minimum.  Water lines between 4 inches and 12 inches (100 mm and 300 mm) shall be ductile iron pipe (AWWA C151) or PVC pressure pipe (AWWA 900 DR18).  Water lines placed above ground or in a trench shall be flanged ductile iron pipe (AWWA C115).  Fittings shall be ductile iron (AWWA C110 or AWWA C153) with rubber sealed gasket joints (AWWA C115).  Piping and fittings for ductile iron pipe shall have cement-mortar lining (AWWA C104).

H501001 1.2 VALVES

H501001 1.2.1 Gate Valves

Provide gate valves conforming to AWWA C509, nonrising stem type with flanged ends.  Body, bonnet and gate shall be of ductile iron.  Valves shall open by counterclockwise rotation of the valve stem.  Stuffing boxes shall have O-ring stem seals.  Stuffing boxes shall be bolted and constructed so as to permit easy removal of parts for repair.  Bronze used in valves shall be Grade A, Grade D or Grade E as specified in AWWA C509.  Valves shall have protective epoxy interior coating conforming to AWWA C550.

H501001 1.3 BACKFLOW PREVENTERS

Provide reduced pressure principle type backflow preventers, with epoxy coated and lined ductile iron bodies, replaceable bronze seats, stainless steel internal parts, nonrising stem gate shut-off valves, and suitable for pressures up to 175 psi (1,200 kPa) at 110 degrees F (43 degrees C).

H501001 1.4 PRESSURE REGULATORS

Provide adjustable pressure regulator to reduce incoming water pressure to level specified in the "Portable Water" paragraph of ESR Section H50, Waterfront Utilitiesin Part 3.

H501001 1.5 UTILITY STATION PIPING AND OUTLET

Piping and outlets shall be in accordance with UFC 4-150-02 or as shown in RFP drawings provided in Part 6.

H501002 SALTWATER

*************************************************************************** 
NOTE:  For project with saltwater system add requirements below.
***************************************************************************

Not used.

H501003 SANITARY SEWER

Requirements for sanitary sewer on pier/wharf are provided below.  Additional requirements are provided in the "Sanitary Sewer Piping" and "Sanitary Sewer Manholes & Cleanouts" paragraphs in PTS Section G30, Site Civil/Mechanical Utilities.

H501003 1.1 PIPING

Piping shall be ductile iron, flanged, conforming to AWWA C115/A21.15, Thickness Class 56.  Fittings shall conform to AWWA C110/A21.10 or AWWA C153/A21.53 and shall have a pressure rating at least equivalent to that of the pipe.  Pipe and fittings shall have a ceramic epoxy internal lining resistant to chemical attack.

H501003 1.2 VALVES

H501003 1.2.1 Plug Valves

Provide plug valves with cast iron bodies, MSS SP-78.  Valves shall be rated for at least 175 psi (1,200 kPa) at 140 degrees F (60 degrees C). Valves and operators shall be designed for outdoor service.  Provide valve with internal lining or coating compatible with ship and submarine sewage discharge.

H501003 1.2.2 Check Valves

Provide swing type check valve with flanged ends.  Valves shall be designed for outdoor service.  Valve materials shall be compatible with ship and submarine sewage discharge.

H501003 1.3 CAMLOCK HOSE COUPLING

Provide camlock hose coupling with stainless steel coupler body, Viton gasket, and twin cam arms with finger rings and stainless steel pins.  Coupling shall have a pressure rating of at least 145 psi (1,000 kPa).  Provide matching stainless steel plug with stainless steel connecting chain.

H501004 BILGE AND OILY WASTE

H501004 1.1 PIPING

Piping shall be ductile iron, flanged, conforming to AWWA C115/A21.15, Thickness Class 56.  Fittings shall conform to AWWA C110/A21.10 or AWWA C153/A21.53 and shall have a pressure rating at least equivalent to that of the pipe.  Pipe and fittings shall have a ceramic epoxy internal lining resistant to chemical attack.

H501004 1.2 VALVES

H501004 1.2.1 Plug Valves

Provide plug valves with cast iron bodies, MSS SP-78.  Valves shall be rated for at least 175 psi (1,200 kPa) at 140 degrees F (60 degrees C). Valves and operators shall be designed for outdoor service.  Provide valve with internal lining or coating compatible with ship and submarine bilge and oily waste discharge.

H501004 1.3 CAMLOCK HOSE COUPLING

Provide camlock hose coupling with stainless steel coupler body, Viton gasket, and twin cam arms with finger rings and stainless steel pins.  Coupling shall have a pressure rating of at least 145 psi (1,000 kPa).  Provide matching stainless steel plug with stainless steel connecting chain.

H501005 STEAM

*************************************************************************** 
NOTE:  For project with steam system add requirements below.
***************************************************************************

Not used.

H501006 COMPRESSED AIR

*************************************************************************** 
NOTE:  For project with high pressure or low pressure compressed air system add requirements below.
***************************************************************************

Not used.

H501090 OTHER CIVIL/MECHANICAL UTILITIES

*************************************************************************** 
NOTE:  For project with other civil/mechanical systems add requirements below.
***************************************************************************

Not used.

H501091 MISCELLANEOUS MATERIAL

H501091 1.1 PIPE GUARDRAILS

Provide Schedule 80 pipe guardrails of stainless steel, ASTM A 312/A 312 M, Type 316L, or of galvanized and coated steel, with butt welding fittings of the same material and weight of the piping.

H501091 1.2 PIPE HANGERS AND SUPPORTS

Pipe hangers and supports shall conform with MSS SP-58 and MSS SP-69 and shall be of Type 316 or Type 316L stainless steel or galvanized steel.

H501091 1.3 HARDWARE

Hardware, including bolts, nuts, washers, anchors and screws, shall be of Type 316 stainless steel or galvanized steel.

H501091 1.4 MISCELLANEOUS METAL

Miscellaneous metal shall be standard mill finished structural steel shapes, galvanized ASTM A 36/ASTM A 36M steel, or Type 316L stainless steel.

H5020 ELECTRICAL UTILITIES

H5020 1.1 DUCT/CONDUIT PLACEMENT

Ducts and conduits located on elevated deck shall be embedded in the concrete deck.  As an alternative, electrical cables can be contained inside concrete jackets supported below the deck.

H502001 ELECTRICAL POWER DISTRIBUTION

H502001 1.1 ELECTRICAL POWER DISTRIBUTION

Waterfront electrical power distribution systems may include the primary system to the substation and the secondary system that serves electrical power outlet assemblies located on the wharf/pier.

Electrical power distribution shall be in accordance with the requirements of the applicable portion of the "Electrical Distribution" paragraph in PTS Section G40, Site Electrical Utilities.

H502001 1.2 ELECTRICAL POWER OUTLET ASSEMBLIES

Refer to the "Utility Mounds" paragraph in PTS Section H10, Waterfront Structures, for enclosure for electrical power outlet assembly.

The Designer of Record shall utilize UFGS Section 26 05 33, Dockside Power Connection Stations, for work related to waterfront electrical power outlet assemblies.  Multiple three phase, three wire power receptacles suitable for the power ratings specified in the "Electrical Power Distribution" paragraph of ESR Section H50, Waterfront Utilitiesin Part 3 shall be provided.  These power outlet assemblies shall be served by substations with 3 phase, 3 wire delta secondaries.  Each receptacle at the power outlet assembly shall be supplied by a power circuit breaker that is capable of delivering the specified amperes continuously with adequate long time trip rating to allow continuous operation at specified amperes without nuisance tripping.  Provide remote controls for each circuit breaker serving share power receptacles.  Provide controls for primary and secondary main circuit breakers at the electrical power outlet assemblies served.

Industrial power outlets shall be provided for portable equipment used at pier side.  Industrial power outlets shall include 3 phase 4 wire receptacles and 3 wire receptacles for the specified voltages, and 115 volt convenience receptacles.  Industrial power outlets shall be served from a substation or transformer with grounded neutral secondary.

*************************************************************************** 
NOTE:  Add requirements for other power outlet assemblies.
***************************************************************************

H502002 TELECOMMUNICATION

Refer to the "Utility Mounds" paragraph in PTS Section H10, Waterfront Structures, for enclosure for telecommunication stations.

Refer to the "Site Communication and Security" paragraph in PTS Section G40, Site Electrical Utilities, for requirements for Cable, wiring, ductbanks, manholes and handholes.

H502003 LIGHTING

Refer to the "Site Lighting" paragraph in PTS Section G40, Site Electrical Utilities, for requirements for over deck lighting.

Provide lighting fixtures mounted on high mast poles.

Provide a computer model of the illumination system using photometric data prepared for the fixture by an independent testing laboratory.  Follow IES standards for preparation of the computer model.  Adjust and modify the design to provide the illumination required. The corrosion protection features shall be suitable for the environmental condition at the site.

H502004 LIGHTNING PROTECTION

Lightning protection system shall be catenary wire type that complies with NFPA 780, MIL-HDBk-1004/6, Lightning Protection, and NAVSEA OP 5 Chapter 6, Lightning Protection.  Protection system shall be design for protection of ordnance that is placed on the pier/wharf.  Provide primary and secondary ground wires and means for connecting portable equipment to the grounding system.  Material used shall be suitable for the environmental conditions at the site.

H502005 ELECTRICAL POWER CABLE BOOMS FOR BERTHING OF SUBMARINES

*************************************************************************** 
NOTE:  The following requirements are applicable only to submarine berthing wharf/pier project that includes electrical power booms.
***************************************************************************

Function of the power boom is to support and deliver power cables from the on pier/wharf power outlet assembly to the points of power connection on the berthed submarine.  Locations of the power booms and the ranch of operation are as shown on RFP drawings provided in Part 6.

The power boom shall be of galvanized steel construction with proper corrosion protection coating meeting the requirements of UFGS Section 09 97 13.26, Coating of Steel Waterfront Structure.  Bolts, nuts and washers shall be hot deep galvanized.  When the boom is under its stowed position at the pier/wharf or when the boom is positioned to connect the cables to the submarine, the boom shall be secured from unexpected movement in both horizontal and vertical directions.  Both horizontal and vertical movements of the boom shall be activated manually with the assistance of power, mechanical or hydraulic device.  Safeguard shall be provided to preclude simultaneous movement in different directions and uncontrolled movement while the boom is in motion.

The power cable shall be supported on a cable tray in the boom with means of delivering the cables to the submarine at different locations as shown on RFP drawings provided in Part 6.  Use of electrical hoist may be allowed.

All electrical or hydraulic components shall be suitable for outdoor services in marine environment.  The rate of movement at the end of the boom shall be limited to 8 feet/minute (2.5 meters/minute).  Moving elements that involve metal-to-metal contact shall have friction reduction components (such as Teflon coatings and bronze bushings).

Structural design requirements for the power boom shall be in accordance with PTS Section H10, Waterfront Structure.

H502090 OTHER ELECTRICAL UTILITIES

Not used.

H5030 WATERFRONT FIRE PROTECTION

H503001 FIRE PROTECTION WATER

H503002 FIRE ALARM

---End of Section---