| GATEHOUSE – OBSERVATION AREA |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Serves as the central control center for the ECF and provides shelter for security personnel. Special Dimensions: [Determined by the number of personnel to be served and site requirements.] Minimum Ceiling Height: Acoustics: 39 STC Access: Base Security Personnel Number of Occupants: Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C103008 | Counters |  |  | Provide [24”] [30”] counter top and back splashes necessary to accommodate observation operations. [Solid Acrylic] [Plastic Laminate]. |
| C103009 | Cabinets |  |  | Cabinet and millwork [freestanding] [below] items with associated accessories. AWI [Custom] [Premium] grade. All exposed surfaces will be [covered with high pressure plastic laminate clad] or [hardwood veneer with exposed edges of solid hardwood] |
| C3010 | Wall finishes |  |  | Egg-shell latex painted [CMU] [GWB] |
| C3020 | Floor Finishes |  |  | [Sheet] [Linoleum]] [[Vinyl] tile]. |
| C3030 | Ceiling Finishes |  |  | Moisture resistant [ACP] [GWB]. |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | [general purpose receptacle] [workstation receptacles] [connections for MEP equipment: [unit heater][air conditioner][security system][control panels][UPS][. . .]] |
| D502002 | Lighting Equipment |  |  | Provide [specialty lighting: [night vision red light]]. Provide lighting control:[ [full-dimming ballast control device][stepped-dimming ballast]] [Provide task lighting at counter] |
| D503001 | Telecommunications Systems |  |  | Provide [phone outlets][data outlets] |
| D503003 | Intercommunication Systems |  |  | [Coordinate requirements with Part 3, chapter 6] Provide two-way communications between [Gatehouse ,] [Sentry/Guard Booth ,] [Overwatch Position ,] Large Commercial Vehicle/Truck Inspection Facilities, ][ID stations,] [Visitor’s Center] [. . . ] |
| D503005 | Security Systems |  |  | Provide [outlets][backboxes][raceways][devices][alarms] [CCTV cameras] to support the security system. [Coordinate requirements with UFC-4-022-01 and Part 3, chapter 6] |
| D509002 | Emergency Lighting and Power |  |  | Provide emergency lighting via [connection to generator system] [integral battery packs] [battery units] Provide emergency power via [connection to generator system] [connection to central UPS system] [local UPS] [coordinate requirements with Part 3, chapter 6] |
| E10 | Equipment |  |  | The Observation operations shall include the following Control center [built-in casework]; [computers and monitors] [, two-way radios] [, and] [audio equipment]. |
| E20 | Furnishings |  |  | Provide ergonomically designed chairs to accommodate number of personnel. |
| G403008 | Communication for Active Barrier Systems |  |  | [Provide communications to operate the [active wedge barrier[s]][pop-up bollards][net barrier[s]. Include all conduit and wiring, underground structures, termination equipment, [poles and structures], as required for a complete and usable system.] |

[

| GATEHOUSE – TOILET ROOM |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Staff use Special Dimensions: Minimum Ceiling Height: Acoustics: Access: Staff Number of Occupants: Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C10 | Interior Construction |  |  | [Provide [unisex] [men’s and women’s] lavatory and water closet.] |
| C103002 | Toilet Accessories |  |  | Provide toilet paper holders [roll] [towel] dispensers, mirror, and waste receptacles. |
| C3010 | Wall Finishes |  |  | Provide [[Ceramic tile] [wainscot]] [moisture resistant GWB] [glazed wall coating] [CMU] |
| C3020 | Floor Finishes |  |  | Provide ceramic tile |
| C3030 | Ceiling Finishes |  |  | Provide Egg-shell latex painted moisture resistant [GWB] |
| D2010 | Plumbing Fixtures |  |  | [Coordinate requirements with UFC 4-722-01] |
| D203003 | Other Plumbing Systems |  |  | [Provide a floor drain] |
| D304007 | HVAC – Exhaust Systems |  |  | Provide negative pressure with a [dedicated exhaust system ] [or] [tie into the central building exhaust system] vented to the outdoors[Provide exhaust air rate per UFC 3-400-10N] |
| D40 | Fire Protection |  |  |  |
| D502001 | Branch Wiring: Receptacles and Equipment Connections |  |  | Provide [GFI receptacle at counter] [general purpose receptacle[s]][ and][ exhaust fan]. |
| D502002 | Lighting Equipment |  |  | Provide [ceiling mounted] [and/or] [wall light above counter]. [Provide occupancy sensor.] |
| E10 | Equipment |  |  |  |
| E20 | Furnishings |  |  |  |

]

[

| GATEHOUSE – ELECTRICAL ROOM |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Provide location for main electric panel boards. Special Dimensions: Minimum Ceiling Height: Acoustics: 52 STC Access: Number of Occupants: Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C3010 | Wall finishes |  |  | Provide Egg-shell latex painted [CMU] [GWB] |
| C3020 | Floor Finishes |  |  | Provide [VCT] [Sealed Concrete] |
| C3030 | Ceiling Finishes |  |  | Provide Moisture resistant [GWB]. |
| D304007 | HVAC |  |  | [Provide ventilation per UFC 3-400-10N] |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | Provide [general purpose receptacle] [connections for MEP equipment: [unit heater] [exhaust fan] [control panels] [. . .]. |
| D502002 | Lighting Equipment |  |  | Provide occupancy sensor |
| D503001 | Telecommunication Systems |  |  | Provide [wall phone outlet][data outlet for DDC system] |
| D509002 | Emergency Lighting and Power |  |  | Provide emergency lighting via [connection to generator system] [integral battery packs] [battery units]. Provide emergency power via [connection to generator system] [connection to central UPS system]. [Coordinate requirements with Part 3, chapter 6.] |

]

[

| GATEHOUSE – STORAGE ROOM |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: General Storage. Special Dimensions: Minimum Ceiling Height: Acoustics: 52 STC Access: Number of Occupants: Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C10 | Interior Construction |  |  |  |
| C3010 | Wall finishes |  |  | Egg-shell latex painted [CMU] [GWB] |
| C3020 | Floor Finishes |  |  | Provide [VCT] [Sealed Concrete] |
| C3030 | Ceiling Finishes |  |  | Provide Moisture resistant [GWB]. |
| D304007 | HVAC |  |  | [Provide ventilation per UFC 3-400-10N] |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | [Provide general purpose receptacle] [Provide connections for MEP equipment: [unit heater] [exhaust fan] [control panels] [. . .] |
| D502002 | Lighting Equipment |  |  | Provide occupancy sensor |
| E10 | Equipment |  |  | Provide equipment to accommodate traffic control devices, weapons and personnel storage |

]

[

| SENTRY/GUARD BOOTH |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Provide one or two guards with protection against the weather and potential threats. Special Dimensions: [Must fit within the median strip or channelization island between traffic lanes.] Minimum Ceiling Height: Acoustics: Access: Number of Occupants: [2] Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C103008 | Counters |  |  | Provide [18”] [24”] Stainless Steel Counter tops and back splashes necessary to accommodate guard operations . |
| C3010 | Wall finishes |  |  | [Latex] [epoxy] painted CMU |
| C3020 | Floor Finishes |  |  | Provide [Sealed Concrete] [Exposed] |
| C3030 | Ceiling Finishes |  |  | Provide Weather-resistant Metal Lay-in Ceiling grid system |
| D305002 | HVAC: Unit Heaters |  |  | [Provide [electric] [gas fired] unit heaters] |
| D501004 | Electrical distribution equipment |  |  | [Provide panelboard] |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | [Provide GFI general purpose receptacle] [Provide connections for MEP equipment: [unit heater] [exhaust fan] [control panels] [. . .]] |
| D502002 | Lighting Equipment |  |  | Provide [specialty lighting: [night vision red light]]. Provide lighting control:[ [full-dimming ballast control device][stepped-dimming ballast]] [Provide [switch] [occupancy sensor]] [control from gate house] |
| D503001 | Telecommunication Systems |  |  | Provide [phone outlet][data outlet] |
| D503003 | Intercommunication support systems |  |  | Provide two-way communications between [Gatehouse ,] [Sentry/Guard Booth ,] [Overwatch Position ,] Large Commercial Vehicle/Truck Inspection Facilities, ][ID stations,] [Visitor’s Center] [. . . ] [coordinate requirements with Part 3, chapter 6] |
| D503005 | Security Systems |  |  | Provide [outlets][backboxes][raceways][devices][alarms] [CCTV cameras] to support the security system [coordinate requirements with UFC-4-022-01 and Part 3, chapter 6] |
| D509002 | Emergency Lighting and Power |  |  | [Provide emergency lighting via [connection to generator system]] Provide emergency power via [connection to generator system] [connection to central UPS system] [Coordinate requirements with Part 3, chapter 6] |

]

[

| OVERHEAD CANOPY |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Special Dimensions: Minimum Ceiling Height: Acoustics: Access: Number of Occupants: Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C3030 | Ceiling Finishes |  |  | Provide Exterior grade Latex painted exterior grade GWB |
| D305002 | HVAC: Unit Heaters |  |  | [Provide [electric] [gas fired] unit heaters [and] [or] [infrared] heaters] |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | [GFI general purpose receptacle] [Provide connections for MEP equipment: [unit heaters] [snow melt system] [. . .]] |
| D502002 | Lighting Equipment |  |  | Provide [HID] [Fluorescent] fixtures Lighting control: [lighting contactor via [photocell] [and] [time clock]] [switch within Observation Room] [. . .] |
| D502002 | Lighting Equipment |  |  | Provide LED signal lights to indicate lane open status, mounted on the Canopy over each lane of traffic. |
| D503003 | Intercommunication support systems |  |  | Provide two-way communications between [Gatehouse ,] [Sentry/Guard Booth ,] [Overwatch Position ,] Large Commercial Vehicle/Truck Inspection Facilities, ][ID stations,] [Visitor’s Center] [. . . ] |
| D503005 | Security Systems |  |  | Provide [outlets][backboxes][raceways][devices][alarms] [CCTV cameras] to support the security system [Coordinate requirements with UFC-4-022-01 and Part 3, chapter 6] |
| D509002 | Emergency Lighting and Power |  |  | [Provide emergency lighting via [connection to generator system]] Provide emergency power via [connection to generator system] [connection to central UPS system] [coordinate requirements with Part 3, chapter 6] |
| D509004 | Lightning Protection |  |  | [Provide lightning protection system] [coordinate requirements with Part 3, chapter 6] |

| G403007 | Electronic Security System |  |  | [Provide the following security equipment in each lane of traffic within the Canopy: [Non-traffic rated Gate Arm] [Vehicle Loop Detectors, pre and post authorization] [Card Reader (CR) – Located on pedestal.] [Camera/Intercom – Co-located with CR for communication with sentry in Gate house.] [RFID Reader] [Traffic Light – Physically located on the Gate Arm Controller.] [Photo Eye Detector - Physically located on the Gate Arm Controller.]] |
| --- | --- | --- | --- | --- |

]

[

| OVERWATCH POSITION – GUARD ROOM |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Provide base security personnel with an elevated position with a direct line of sight to the access control zone of the ECF including identification and inspection areas to facilitate a response to a threat. Special Dimensions: Minimum Ceiling Height: Acoustics: 39 STC Access: Base Security Personnel Number of Occupants: [2] Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C103008 | Counters |  |  | Provide 24” deep counter tops and back splashes necessary to accommodate observation operations. [Solid Acrylic] [Plastic Laminate]. |
| C103009 | Cabinets |  |  | Cabinet and millwork [freestanding] [below] items with associated accessories. AWI [Custom] [Premium] grade. All exposed surfaces will be [covered with high pressure plastic laminate clad] or [hardwood veneer with exposed edges of solid hardwood |
| C3010 | Wall finishes |  |  | Provide [moisture resistant] gypsum wall board |
| C3020 | Floor Finishes |  |  | Provide [sheet] [linoleum]] [[Vinyl] [linoleum] tile]. |
| C3030 | Ceiling Finishes |  |  | Provide [Moisture resistant] [ACP] [GWB]. |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | Provide [general purpose receptacle] [workstation receptacles] [Provide connections for MEP equipment: [unit heater][air conditioner][security system][control panels][UPS][. . .]][panelboard] |
| D502002 | Lighting Equipment |  |  | [Provide specialty lighting: [night vision red light]] Provide lighting control:[ [full-dimming ballast control device][stepped-dimming ballast]] [Provide task lighting at counter] |
| D503001 | Telecommunications Systems |  |  | Provide [phone outlets][data outlets] |
| D503003 | Intercommunication Systems |  |  | [Coordinate requirements with Part 3, chapter 6] Provide two-way communications between [Gatehouse ,] [Sentry/Guard Booth ,] [Overwatch Position ,] Large Commercial Vehicle/Truck Inspection Facilities, ][ID stations,] [Visitor’s Center] [. . . ] |
| D503005 | Security Systems |  |  | Provide [outlets][backboxes][raceways][devices][alarms] [CCTV cameras] to support the security system [coordinate requirements with UFC-4-022-01 and Part 3, chapter 6] |
| D509002 | Emergency Lighting and Power |  |  | Provide emergency lighting via [connection to generator system] [integral battery packs] [battery units] Provide emergency power via [connection to generator system] [connection to central UPS system] [local UPS] [Coordinate requirements with Part 3, chapter 6] |
| D509004 | Lighting Protection |  |  | [Coordinate requirements with Part 3, chapter 6] |

| E20 | Furnishings |  |  | Provide ergonomically designed chairs to accommodate [__] personnel |
| --- | --- | --- | --- | --- |
| G403008 | Communication for Active Barrier Systems |  |  | [Provide communications to operate the [active wedge barrier[s]][pop-up bollards][net barrier[s]. Include all conduit and wiring, underground structures, termination equipment, [poles and structures], as required for a complete and usable system.] |

]

[

| OVERWATCH POSITION – STORAGE/EQUIPMENT ROOM |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Store electronics and other equipment necessary to sustain the overwatch positions communications, lighting, heating and air conditioning. Special Dimensions: Minimum Ceiling Height: Acoustics: 52 STC Access: Number of Occupants: [2] Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C1020 | Floor Access door |  |  | [At Tower Type facility Provide floor door/ Access panel From Storage Equipment Room to Over watch Room] |
| C20 | Stairs |  |  | [[Interior stairs shall be constructed of [steel] [steel with concrete filled pans] [or] [cast-in-place concrete]] [Exterior stairs shall be constructed of [galvanized steel] [or] [cast-in-place reinforced concrete]. Provide handrails, guardrails and accessories |
| C3010 | Wall finishes |  |  | Egg-shell latex painted [CMU] |
| C3020 | Floor Finishes |  |  | Provide [Sealed Concrete] |
| C3030 | Ceiling Finishes |  |  | Exposed Ceiling |
| D304007 | HVAC |  |  | [Provide ventilation per UFC 3-400-10N] |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | [Provide general purpose receptacle] [Provide connections for MEP equipment: [unit heater] [exhaust fan] [control panels] [. . .] |
| D502002 | Lighting Equipment |  |  | Provide occupancy sensor |
| D503001 | Voice & Data equipment |  |  | Provide [wall phone outlet][data outlet for DDC system] |
| E20 | Furnishings |  |  |  |

]

[

| VISITOR CENTER – WAITING AREA |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Provide a comfortable environment with adequate seating for visitors to await processing. Special Dimensions: Minimum Ceiling Height: Acoustics: Access: Customers and staff, must be compliant with ADAAG Number of Occupants: [Based on peak hourly requirements] Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C10 | Interior Requirements |  |  | Provide tack boards. [Glass-enclosed bulletin board] Recessed display case.] [Vestibule at main entry] [wall mounted television][tackboards]. |
| C3010 | Wall finishes |  |  | Provide Egg-shell latex painted [GWB] [CMU] [Vinyl wall covering] |
| C3020 | Floor Finishes |  |  | Provide [sheet] [linoleum]] [[Vinyl] [linoleum] tile] [vinyl base] [Stone] [Quarry tile] [Stone base] Tile base]. |
| C3030 | Ceiling Finishes |  |  | Provide [ACP] [GWB]. |
| D201006 | Plumbing: Drinking Fountains and Electric Water Coolers |  |  | [Provide a [electric water cooler] [drinking fountain] [with bubbler] and [ADA compliant] |
| D502001 | Branch wiring - Receptacles and equipment connections |  |  | Provide [general purpose receptacle] [and][reception desk receptacle] [Provide connections for MEP equipment: [TV] [HVAC equipment] [water bubbler] [water cooler] [vending machines] [coffee maker] [ATM] [. . .] |
| D502002 | Lighting Equipment |  |  | Provide [Night lighting fixtures] [Switch located in staff area} |
| D503001 | Telecommunication Systems |  |  | Provide [phone outlet][data outlet] [pay phone] |
| D503004 | Television Systems |  |  | [Provide a CATV outlet [consisting of empty raceways and outlet boxes to enable system installation by the commercial CATV supplier.] |
| D503005 | Security Systems |  |  | Provide [outlets][backboxes][raceways][devices][alarms] [CCTV cameras] to support the security system [coordinate requirements with UFC-4-022-01 and Part 3, chapter 6] |
| E10 | Equipment |  |  | Provide Vending Machines, Vendor Data Entry Station and Photo Background walls |
| E20 | Furnishings |  |  | Provide ergonomically designed chairs and furnishings to accommodate [__] visitors [Vending machines] |

]

[

| VISITOR CENTER – SERVICE COUNTER |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Special Dimensions: Minimum Ceiling Height: Acoustics: Access: Staff and customers, must be compliant with ADAAG Number of Occupants: [Based on peak hourly requirements] Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C103008 | Counters |  |  | Provide 24” deep counter tops and back splashes necessary to accommodate service operations, that includes Photo area and Pass and Decal area. [Solid Acrylic] [Plastic Laminate]. |
| C103009 | Cabinets |  |  | Cabinet and millwork [freestanding] [below] items with associated accessories. AWI [Custom] [Premium] grade. All exposed surfaces will be [covered with high pressure plastic laminate clad] or [hardwood veneer with exposed edges of solid hardwood] |
| C3010 | Wall finishes |  |  | Egg-shell latex painted [CMU] [GWB] |
| C3020 | Floor Finishes |  |  | Provide [sheet] [linoleum]] [[Vinyl] [linoleum] tile] [vinyl base] |
| C3030 | Ceiling Finishes |  |  | [ACP] [GWB]. |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | [Provide general purpose receptacle] [workstation receptacles] [Provide connections for MEP equipment: [unit heater][air conditioner][security system][control panels][UPS][. . .]] |
| D502002 | Lighting Equipment |  |  | Provide lighting control:[ [single switch] [full-dimming ballast control device][stepped-dimming ballast]] [Provide task lighting at counter] |
| D503001 | Telecommunications Systems |  |  | Provide [phone outlets][data outlets] |
| D503003 | Intercommunication Systems |  |  | [Coordinate requirements with Part 3, chapter 6] Provide two-way communications between [Gatehouse ,] [Sentry/Guard Booth ,] [Overwatch Position ,] Large Commercial Vehicle/Truck Inspection Facilities, ][ID stations,] [Visitor’s Center] [. . . ] |
| D503005 | Security Systems |  |  | Provide [outlets][backboxes][raceways][devices][alarms] [CCTV cameras] to support the security system [coordinate requirements with UFC-4-022-01 and Part 3, chapter 6] |
| D509002 | Emergency Lighting and Power |  |  | Provide emergency lighting via [connection to generator system] [integral battery packs] [battery units] Provide emergency power via [connection to generator system] [connection to central UPS system] [local UPS] [coordinate requirements with Part 3, chapter 6] |
| E20 | Furnishings |  |  | Provide book cases, ergonomically designed seating. |

]

[

| VISITOR CENTER – ADMINISTRATIVE OFFICE |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Special Dimensions: Minimum Ceiling Height: Acoustics: 39 STC Access: Number of Occupants: Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C3010 | Wall finishes |  |  | Provide Egg-shell latex painted [CMU] [GWB] |
| C3020 | Floor Finishes |  |  | Provide [sheet] [linoleum]] [[Vinyl] [linoleum] tile] [Commercial Carpeting]. |
| C3030 | Ceiling Finishes |  |  | Provide ACT |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | Provide [general purpose receptacle] [workstation receptacles]. [Provide Connections for MEP equipment: [unit heater][air conditioner][security system][control panels][UPS][. . .]] |
| D502002 | Lighting Equipment |  |  | Provide lighting control:[ [single switch] [full-dimming ballast control device][stepped-dimming ballast]] [Provide task lighting at counter] |
| D503001 | Telecommunications Systems |  |  | Provide [phone outlets][data outlets] |
| D503003 | Intercommunication Systems |  |  | [Coordinate requirements with Part 3, chapter 6] Provide two-way communications between [Gatehouse ,] [Sentry/Guard Booth ,] [Overwatch Position ,] Large Commercial Vehicle/Truck Inspection Facilities, ][ID stations,] [Visitor’s Center] [. . . ] |
| D503005 | Security Systems |  |  | Provide [outlets][backboxes][raceways][devices][alarms] [CCTV cameras] to support the security system [coordinate requirements with UFC-4-022-01 and Part 3, chapter 6] |
| D509002 | Emergency Lighting and Power |  |  | Provide emergency lighting via [connection to generator system] [integral battery packs] [battery units] Provide emergency power via [connection to generator system] [connection to central UPS system] [local UPS] [coordinate requirements with Part 3, chapter 6] |
| E20 | Furnishings |  |  | Provide office desk, ergonomically designed office chair, file cabinet, book shelf, desk lamp and side chair [and credenza] [and] two additional side chairs] |

]

[

| VISITOR CENTER – BREAK ROOM |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Provide refrigerator, microwave, sink and seating for Entry Control Facility Staff Special Dimensions: Minimum Ceiling Height: Acoustics: Access: Number of Occupants: Other/special requirements: Must be out of the direct line of sight of the waiting/seating area. |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C103008 | Counters |  |  | Provide 24” deep [Solid Acrylic] [Plastic Laminate] counter tops and splashes. |
| C103009 | Cabinets |  |  | Provide base and wall cabinet and millwork [freestanding] [below] items with associated accessories. AWI [Custom] [Premium] grade. All exposed surfaces will be [covered with high pressure plastic laminate clad] or [hardwood veneer with exposed edges of solid hardwood] |
| C3010 | Wall finishes |  |  | Provide Egg-shell latex painted [CMU] [GWB] |
| C3020 | Floor Finishes |  |  | Provide [sheet] [linoleum]] [[Vinyl] [linoleum] tile]. |
| C3030 | Ceiling Finishes |  |  | Provide ACP |
| D20 | Plumbing: General |  |  | [Coordinate requirements with UFC 4-722-01 [and] [LEED requirements]Provide connections for [dishwasher], [coffee maker] |
| D201004 | Plumbing: Sink |  |  | Provide countertop deep sink [with two compartments] [and waste disposer.] |
| D202005 | Plumbing: Specialties |  |  | [Provide icemaker box] |
| D203003 | Plumbing: Floor Drain |  |  | [Provide floor drain] |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | Provide [general purpose receptacle] [GFI receptacles above counter]. Provide [receptacles and dedicated circuits for each refrigerator, microwave and vending machine] [Provide connections for MEP equipment [HVAC equipment [garbage disposal] [icemaker box] [. . .]] |
| D502002 | Lighting Equipment |  |  | Provide lighting control:[ [single switch] [full-dimming ballast control device][stepped-dimming ballast]] [Provide task lighting at counter] |
| D503001 | Intercommunication Systems |  |  | Provide [wall phone outlet] |
| D509002 | Emergency Lighting and Power |  |  | Provide emergency lighting via [connection to generator system] [integral battery packs] [battery units] [coordinate requirements with Part 3, chapter 6] |
| E20 | Furnishings |  |  | Provide table and ergonomically designed chairs to accommodate [__] personnel, waste receptacle, microwave refrigerator.[Tackboards] |

]

[

| VISITOR CENTER – TOILET ROOMS |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Public use, ADA facilities Special Dimensions: Minimum Ceiling Height: Acoustics: Access: Customers and Staff Number of Occupants: [Based on personnel to be served and turnover rate.] Other/special requirements: Provide baby-changing stations in each restroom. |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C10 | Interior Construction |  |  | [Provide lavatories, water closets, urinals and urinal partitions, and toilet accessories as necessary to accommodate the personnel to be served and turnover rate.] |
| C103001 | Toilet Partitions |  |  | Provide [stainless steel] [plastic laminate] [solid plastic] [phenolic core] [or metal with enamel finish] [Stainless steel] toilet partitions in all toilet rooms with more than one water closet or urinal. |
| C103002 | Toilet Accessories |  |  | Provide toilet paper holders [roll] [towel] dispensers, mirror over vanity, and waste receptacles. |
| C103008 | Counters |  |  | Provide 24” deep counter and back splashes [Solid Acrylic] [Plastic Laminate] |
| C103009 | Cabinets |  |  | Vanity type under-counter cabinet and millwork [freestanding] [below] items with associated accessories. AWI [Custom] [Premium] grade. All exposed surfaces will be [covered with high pressure plastic laminate clad] or [hardwood veneer with exposed edges of solid hardwood] |
| C3010 | Wall Finishes |  |  | Provide [[Porcelain tile] [wainscot]] Full height] [moisture resistant, GWB] [glazed wall coating] [CMU] |
| C3020 | Floor Finishes |  |  | Provide Porcelain tile |
| C3030 | Ceiling Finishes |  |  | Provide Egg-shell latex painted moisture resistant [GWB] |
| D2010 | Plumbing Fixtures | See UFC 4-730-10 Chapter 4, and consult with Activity for fixture counts for male/female splits. |  | Provide [wall] [floor] mounted fixtures[with electronic flush control] [Coordinate requirements with UFC 4-722-01 [and] [LEED requirements] |
| D203003 | Plumbing: Floor Drain |  |  | [Provide floor drain] |
| D304007 | HVAC – Exhaust Systems |  |  | Provide negative pressure with a [dedicated exhaust system ] [or] [tie into the central building exhaust system] vented to the outdoors[Provide exhaust air rate per UFC 3-400-10N] |
| D40 | Fire Protection |  |  |  |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | Provide GFI receptacle at counter Provide [general purpose receptacle] [exhaust fan] [. . .] |
| D502002 | Lighting Equipment |  |  | Provide [ceiling][wall] mounted light above counter.] [Provide occupancy sensor] |
| E10 | Equipment |  |  |  |
| E20 | Furnishings |  |  |  |

]

[

| VISITOR CENTER – JANITOR’S CLOSET |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Special Dimensions: Minimum Ceiling Height: Acoustics: Access: Staff Number of Occupants: Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C1030 | Janitor specialties |  |  | Provide Mop holder |
| C3010 | Wall Finishes |  |  | Provide [moisture resistant, mildew-resistant GWB] |
| C3020 | Floor Finishes |  |  | Provide [sheet] [linoleum]] [[Vinyl] [linoleum] tile]. |
| C3030 | Ceiling Finishes |  |  | Provide Egg-shell latex painted moisture resistant [GWB |
| D201004 | Plumbing: Service or Mop Sink |  |  | Provide a [service sink] [mop sink] |
| D203003 | Plumbing: Floor Drain |  |  | [Provide floor drain] |
| D40 | Fire Protection |  |  |  |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | Provide GFI general purpose receptacle [and exhaust fan]. |
| D502002 | Lighting Equipment |  |  | [Provide occupancy sensor] |
| E10 | Equipment |  |  | [Shelving for miscellaneous non-toxic cleaning equipment storage] |
| E20 | Furnishings |  |  |  |

]

[

| LARGE COMM. VEHICLE/TRUCK INSPECTION FACILITIES – INSPECTION OFFICE |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Special Dimensions: Minimum Ceiling Height: Acoustics: 39 STC Access: Number of Occupants: Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C3010 | Wall finishes |  |  | Provide epoxy painted CMU |
| C3020 | Floor Finishes |  |  | Provide sealed concrete surface, [Provide a non-skid, low-maintenance traffic coating]. Slope floor to trench drains. |
| C3030 | Ceiling Finishes |  |  | Coordinate mechanical, electrical and plumbing components. None of the ceiling components can be located below minimum ceiling height. |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | Provide [general purpose receptacle] [workstation receptacles] [Provide connections for MEP equipment: [unit heater][air conditioner][security system][control panels][UPS][. . .]] |
| D502002 | Lighting Equipment |  |  | Provide lighting control:[ [single switch] [full-dimming ballast control device][stepped-dimming ballast]] [Provide task lighting at counter] |
| D503001 | Telecommunications Systems |  |  | Provide [phone outlets][data outlets] |
| D503003 | Intercommunication Systems |  |  | [Coordinate requirements with Part 3, chapter 6] Provide two-way communications between [Gatehouse ,] [Sentry/Guard Booth ,] [Overwatch Position ,] Large Commercial Vehicle/Truck Inspection Facilities, ][ID stations,] [Visitor’s Center] [. . . ] |
| D503005 | Security Systems |  |  | Provide [outlets][backboxes][raceways][devices][alarms] [CCTV cameras] to support the security system [coordinate requirements with UFC-4-022-01 and Part 3, chapter 6] |
| D509002 | Emergency Lighting and Power |  |  | Provide emergency lighting via [connection to generator system] [integral battery packs] [battery units] Provide emergency power via [connection to generator system] [connection to central UPS system] [local UPS] [coordinate requirements with Part 3, chapter 6] |
| E20 | Furnishings |  |  |  |

]

[

| LARGE COMM. VEHICLE/TRUCK INSPECTION FACILITIES – INSPECTION BUILDING |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Space Characteristics |  |  |  |  |
| Function/adjacencies: Special Dimensions: Minimum Ceiling Height: Acoustics: Access: Number of Occupants: Other/special requirements: |  |  |  |  |
| ###### Uniformat Section# | Description | Qty | Size | Specific Requirements |
| C10 | Interior Construction |  |  | Provide epoxy painted CMU |
| C3010 | Wall finishes |  |  | Provide epoxy painted CMU |
| C3020 | Floor Finishes |  |  | Provide [sheet] [linoleum]] [[Vinyl] [linoleum] tile]. |
| C3030 | Ceiling Finishes |  |  | Provide Moisture resistant [ACP] [GWB]. |
| D502001 | Branch Wiring: Receptacles and equipment connections |  |  | Provide [general purpose receptacle] [workstation receptacles] [Provide connections for MEP equipment: [unit heater][air conditioner][security system][control panels][UPS][. . .]] |
| D502002 | Lighting Equipment |  |  | Provide lighting control:[ [single switch] [full-dimming ballast control device][stepped-dimming ballast]] [Provide task lighting at counter] |
| D502002 | Lighting Equipment |  |  | Provide LED signal lights to indicate lane open status, mounted over each lane of traffic. |
| D503001 | Telecommunications Systems |  |  | Provide [phone outlets][data outlets] |
| D503003 | Intercommunication Systems |  |  | [Coordinate requirements with Part 3, chapter 6] Provide two-way communications between [Gatehouse ,] [Sentry/Guard Booth ,] [Overwatch Position ,] Large Commercial Vehicle/Truck Inspection Facilities, ][ID stations,] [Visitor’s Center] [. . . ] |
| D503005 | Security Systems |  |  | Provide [outlets][backboxes][raceways][devices][alarms] [CCTV cameras] to support the security system [Coordinate requirements with UFC-4-022-01 and Part 3, chapter 6] |
| D509002 | Emergency Lighting and Power |  |  | Provide emergency lighting via [connection to generator system] [integral battery packs] [battery units] Provide emergency power via [connection to generator system] [connection to central UPS system] [local UPS] [coordinate requirements with Part 3, chapter 6] |
| E20 | Furnishings |  |  | Provide office desk, ergonomic office chair, file cabinet, book shelf, desk lamp and side chair [and credenza] [and] two additional side chairs] |

]